## 总览 Overview
多肽厂房2（项目139788） |  | Peptide Building 2 (Project 139788)
客户整改问题、设备整改与改造方案 — 截至2026年9月17日 |  | Customer findings, equipment rectification and retroﬁt options – status 17 Sep 2026
本文件为2026-09-17整改工作表的中英双语版：原文保持不变，英文译文写在同一单元格内（短文本用“中文 / English”，长文本按行中英对照）。原表用筛选隐藏的行列仍保持隐藏，版式、配色与甘特图与原表一致。 |  | Bilingual version of the 09-17-2026 rectification working file: the Chinese text is unchanged and the English translation sits in the same cell (“中文 / English” for short text, line-by-line for long text). Rows and columns hidden by filters in the original stay hidden, and layout, colour coding and Gantt bars follow the original.
本工作簿内容 What is in this workbook
供货周期 Lead Times | 两种管道方案的分项供货周期：现有系统全部316L，以及新批次系统部分哈氏合金、部分316L。 | Supplier lead times per item for the two piping scenarios: existing system all-316L, and the new batch system partly Hastelloy / partly 316L.
现有设备替换方案2 Replace Existing | 仅考虑现有设备及管道替换的采购清单（不含新增CIP等），含安装、验证、清洗周期及10月至2月逐日进度。 | Purchasing list for replacing the existing equipment and piping (no new CIP etc.), with the installation, qualification and cleaning durations and the day-by-day schedule from October to February.
新批次方案1全部新购 New System | 全部新购的新做批次配液系统采购清单，按PID图安装。 | Purchasing list for a completely new batch solution preparation system, installed to the P&ID.
方案1 Option 1 Retrofit Only | 仅现状改造以满足客户最新会议需求，约2026年11月30日完成；含改造需求、子方案与逐项进展。 | Modify the existing installation only, to meet the requirements from the latest customer meeting; target completion around 30 Nov 2026. Includes the modification requirement, sub-options and current status per item.
方案2 Option 2 New Batch | 利用多肽3厂房释放的3000L哈氏合金釜新做批次配液系统，并附进度计划。 | New batch solution preparation system reusing the 3000 L Hastelloy reactor released by Peptide Building 3, with the associated schedule.
方案3 Option 3 All New | 储罐、泵与管道全部换新（316L+哈氏合金），并附进度计划。 | All vessels, pumps and piping replaced by new equipment (316L + Hastelloy), with the associated schedule.
客户整改问题评估 Findings | 核心评估表：按设备位号与部件（本体、管路、仪表、泵、阀门）列客户问题、内部整改方案、目前进展及采购、安装、验证清洗周期。 | Core assessment table: per equipment tag and per component (body, piping, instruments, pumps, valves) the customer finding, the internal rectification plan, the current status, and the procurement, installation, qualification and cleaning durations.
前期剩余工作 Open Work | 已完成与未完成的改造施工项，按各轮新增需求列工期、进展、影响因素、供应商与责任人。 | Retrofit work packages already executed and still open, per round of additional requirements, with duration, status, blocking factors, supplier and responsible person.
辅助设备 Auxiliary Equipment | 过滤器、滤芯、局部层流与注射水软管采购清单。 | Purchasing list for filters, cartridges, local laminar flow units and WFI hoses.
阅读说明 How to read the assessment
• 问题按设备位号、再按部件（设备本体、管路、仪表、泵、阀门）归类。 |  | Findings are grouped per equipment tag and then per component: equipment body, piping, instruments, pumps and valves.
• “2D”指死角长度不超过两倍管径。绝大多数问题属于四类：不满足2D、存在死角、非BPE管路、球阀需改隔膜阀。 |  | “2D” is the drainability criterion: a dead leg may not be longer than two pipe diameters. Most findings are either a 2D breach, a dead leg, a non-BPE line, or a ball valve that has to become a diaphragm valve.
• “评估无异常，客户现场提出”指该条来自客户现场排查，我方评估未确认为缺陷。 |  | “Assessment shows no issue; raised by the customer on site” means the point came from the customer walk-down and our own assessment did not confirm a gap.
• 进度表中黄色填充为待采购确认的到货时间；进度假设10月中下旬生产结束后开始改造。 |  | Yellow fills in the schedules mark delivery dates that Purchasing still has to confirm; the schedules assume the retrofit starts after production ends in mid / late October.
• 原表通过筛选隐藏的行列在本版本中仍隐藏；取消筛选或取消隐藏即可查看全部内容。 |  | Rows and columns hidden by filters in the original are still hidden here; clear the filter or unhide them to see the full content.
需客户确认的开放项 Open points that need a customer decision
• 现场多台储罐的TC接口为自行改造，需征求客户意见是否接受。 |  | The TC connections on several vessels on site were made in-house; the customer has to confirm whether they are acceptable.
• 浓盐管道能否用316L替代哈氏合金，直接影响造价与货期。 |  | Whether 316L may be used for the concentrated-salt lines instead of Hastelloy, which drives both cost and lead time.
• 高压制备系统：BPE管路耐压0.7MPa，系统运行7MPa、设计10MPa，快开接口无法替代丝扣与卡套结构。 |  | The high-pressure preparative system: BPE piping is rated 0.7 MPa while the system operates at 7 MPa (design 10 MPa), so quick-connect fittings cannot replace the threaded and compression connections.
• 超滤：搅拌形式、3㎡膜包替代0.6㎡、是否取消V305阀门、甲醇插底管长度。 |  | Ultrafiltration: agitator design, 3 m² Sartorius cassettes instead of 0.6 m², deleting valve V305, and the methanol dip tube length.
• 单轴旋分筛客户尚未评估确认，目前不满足BPE与洁净设计要求。 |  | The single-shaft rotary sifter has not yet been assessed by the customer and currently does not meet the BPE and hygienic design requirements.
缩写 Abbreviations
BPE | ASME BPE 生物工艺设备标准 | ASME BPE, Bioprocessing Equipment standard
2D | 死角长度不超过两倍管径 | Dead leg no longer than two pipe diameters
TC / NA | 卡箍快开接口 / 喇叭口（NA）卫生级接口 | Tri-clamp quick-connect / flare (NA) type sanitary nozzle
IQ / OQ / PQ / EOQ | 安装、运行、性能及强化运行确认 | Installation, operational, performance and enhanced operational qualification
C22 / C276 / HC | 哈氏合金牌号 / 哈氏合金统称 | Hastelloy alloy grades / Hastelloy in general
CNC / C级 / D级 | 非受控洁净区 / 洁净级别 | Controlled not classified area / cleanroom grades
TFF | 切向流过滤（超滤）撬装 | Tangential flow filtration (ultrafiltration) skid
TCU | 温度控制单元 | Temperature control unit
DCS | 集散控制系统 | Distributed control system
WFI / PW | 注射用水 / 纯化水 | Water for injection / purified water
T型阀 T-valve | 罐底阀 / 零死角阀，用于满足2D要求 | Tank bottom or zero-dead-leg valve used to keep the 2D requirement
翻译说明：供应商与人员姓名按音译处理（Yingde、Chengxin、Tongbo、Longma、Xinlai、Watson、Furuide、Yuanxi、Nuomeng、Weiterui、Shouke、Ternp、Tofflon、Yaguang、Sartorius、Ailipu）；设备名称沿用原表位号表；原文有错别字或简写处按其实际含义翻译。 |  | Translation notes: supplier and personnel names are transliterated from the original. Equipment names follow the tag list of the original file; where the Chinese text contained typos or shorthand, the intended meaning was used.

## 供货周期 Lead Times (hidden)
现有制备系统改造-管道全部316L材质 Retrofit of the existing preparation system – all piping in 316L
序号 / No. | 分项 / Item | 材质 / Material | 数量 / Quantity | 货期（天） / Lead time (days) | 备注 / Remarks
1 | 配液罐（BPE） / Solution preparation vessel (BPE) | C22 | 见附件 / See attachment | 100 | 浙江诚信货期 / Lead time from Zhejiang Chengxin | 需要生产确认更换范围？ / Replacement scope to be confirmed by Production?
2 | 离心泵（快开、BPE） / Centrifugal pump (quick-connect, BPE) | 316L | 见附件 / See attachment | 60 | 待定，预估货期 / To be confirmed, estimated lead time | 需要生产确认更换范围？ / Replacement scope to be confirmed by Production?
3 | 质量流量计（快开、BPE） / Mass flow meter (quick-connect, BPE) | 316L | 见附件 / See attachment | 30 | 首科4周、沃森5-6周 / Shouke 4 weeks, Watson 5–6 weeks
4 | 气动隔膜调节阀（快开、BPE） Pneumatic diaphragm control valve (quick-connect, BPE) | 316L | 见附件 / See attachment | 42 | 新莱：防爆气动316L的6周；防爆的气动的特材的10周 Xinlai: 6 weeks for explosion-proof pneumatic 316L; 10 weeks for explosion-proof pneumatic in special alloy
5 | 气动隔膜开关阀（快开、BPE） Pneumatic diaphragm on/off valve (quick-connect, BPE) | 316L | 见附件 / See attachment | 42 | 新莱：防爆气动316L的6周；防爆的气动的特材的10周 Xinlai: 6 weeks for explosion-proof pneumatic 316L; 10 weeks for explosion-proof pneumatic in special alloy
6 | 气动调节阀（快开、BPE） / Pneumatic control valve (quick-connect, BPE) | 316L | 见附件 / See attachment | 42 | 维特瑞6-8周 / Weiterui 6–8 weeks
7 | 气动开关阀（快开、BPE） / Pneumatic on/off valve (quick-connect, BPE) | 316L | 见附件 / See attachment | 49 | 浙江三方7周 / Zhejiang Sanfang 7 weeks
8 | 雷达液位计 / Radar level transmitter | 316L | 见附件 / See attachment | 20 | 福瑞德2-3周 / Furuide 2–3 weeks
9 | 音叉 / Tuning-fork level switch | 316L | 见附件 / See attachment | 20 | 福瑞德2-3周 / Furuide 2–3 weeks
10 | 温度 / Temperature instrument | 316L | 见附件 / See attachment | 20 | 福瑞德2-3周 / Furuide 2–3 weeks
11 | PH / pH instrument | 316L | 见附件 / See attachment | 42 | 特恩普6-8周 / Ternp 6–8 weeks
12 | 压力 / Pressure instrument | 316L | 见附件 / See attachment | 60 | 福瑞德2-3周 / Furuide 2–3 weeks
13 | 手动隔膜阀 / Manual diaphragm valve | 316L | 见附件 / See attachment | 45 | 新莱的手动316L的6周；手动特材的10周 Xinlai: 6 weeks for manual 316L; 10 weeks for manual in special alloy
14 | BPE管道、管件 / BPE piping and fittings | 316L | 见附件 / See attachment | 25 | 源禧3周 / Yuanxi 3 weeks
新做批次制备配液系统改造-管道部分哈氏合金、部分316L材质 Retrofit of the new batch preparation / solution system – piping partly Hastelloy, partly 316L
序号 / No. | 分项 / Item | 材质 / Material | 数量 / Quantity | 货期（天） / Lead time (days) | 备注 / Remarks
1 | 配液罐（BPE） / Solution preparation vessel (BPE) | C22 | 见附件 / See attachment | 100 | 浙江诚信货期 / Lead time from Zhejiang Chengxin
2 | 离心泵（快开、BPE） / Centrifugal pump (quick-connect, BPE) | C22 | 见附件 / See attachment | 75 | 待定，预估货期 / To be confirmed, estimated lead time
3 | 质量流量计（快开、BPE） / Mass flow meter (quick-connect, BPE) | C22 | 见附件 / See attachment | 35 | 沃森5-6周 / Watson 5–6 weeks
4 | 气动隔膜调节阀（快开、BPE） Pneumatic diaphragm control valve (quick-connect, BPE) | C22 | 见附件 / See attachment | 70 | 新莱：防爆气动316L的6周；防爆的气动的特材的10周 Xinlai: 6 weeks for explosion-proof pneumatic 316L; 10 weeks for explosion-proof pneumatic in special alloy
5 | 气动隔膜开关阀（快开、BPE） Pneumatic diaphragm on/off valve (quick-connect, BPE) | C22 | 见附件 / See attachment | 70 | 新莱：防爆气动316L的6周；防爆的气动的特材的10周 Xinlai: 6 weeks for explosion-proof pneumatic 316L; 10 weeks for explosion-proof pneumatic in special alloy
6 | 手动隔膜阀 / Manual diaphragm valve | C22 | 见附件 / See attachment | 70 | 新莱的手动316L的6周；手动特材的10周 Xinlai: 6 weeks for manual 316L; 10 weeks for manual in special alloy
7 | BPE管件 / BPE fittings | C22 | 见附件 / See attachment | 60 | 诺盟8周 / Nuomeng 8 weeks
8 | 离心泵（快开、BPE） / Centrifugal pump (quick-connect, BPE) | 316L | 见附件 / See attachment | 60 | 待定，预估货期 / To be confirmed, estimated lead time
9 | 质量流量计（快开、BPE） / Mass flow meter (quick-connect, BPE) | 316L | 见附件 / See attachment | 35 | 沃森5-6周 / Watson 5–6 weeks
10 | 气动隔膜调节阀（快开、BPE） Pneumatic diaphragm control valve (quick-connect, BPE) | 316L | 见附件 / See attachment | 42 | 新莱：防爆气动316L的6周；防爆的气动的特材的10周 Xinlai: 6 weeks for explosion-proof pneumatic 316L; 10 weeks for explosion-proof pneumatic in special alloy
11 | 气动隔膜开关阀（快开、BPE） Pneumatic diaphragm on/off valve (quick-connect, BPE) | 316L | 见附件 / See attachment | 42 | 新莱：防爆气动316L的6周；防爆的气动的特材的10周 Xinlai: 6 weeks for explosion-proof pneumatic 316L; 10 weeks for explosion-proof pneumatic in special alloy
12 | 气动调节阀（快开、BPE） / Pneumatic control valve (quick-connect, BPE) | 316L | 见附件 / See attachment | 42 | 维特瑞6-8周 / Weiterui 6–8 weeks
13 | 气动开关阀（快开、BPE） / Pneumatic on/off valve (quick-connect, BPE) | 316L | 见附件 / See attachment | 49 | 浙江三方7周 / Zhejiang Sanfang 7 weeks
14 | 雷达液位计 / Radar level transmitter | 316L | 见附件 / See attachment | 20 | 福瑞德2-3周 / Furuide 2–3 weeks
15 | 音叉 / Tuning-fork level switch | 316L | 见附件 / See attachment | 20 | 福瑞德2-3周 / Furuide 2–3 weeks
16 | 温度 / Temperature instrument | 316L | 见附件 / See attachment | 20 | 福瑞德2-3周 / Furuide 2–3 weeks
17 | PH / pH instrument | 316L | 见附件 / See attachment | 42 | 特恩普6-8周 / Ternp 6–8 weeks
18 | 压力 / Pressure instrument | 316L | 见附件 / See attachment | 60 | 福瑞德2-3周 / Furuide 2–3 weeks
19 | 手动隔膜阀 / Manual diaphragm valve | 316L | 见附件 / See attachment | 45 | 新莱的手动316L的6周；手动特材的10周 Xinlai: 6 weeks for manual 316L; 10 weeks for manual in special alloy
20 | BPE管道、管件 / BPE piping and fittings | 316L | 见附件 / See attachment | 25 | 源禧3周 / Yuanxi 3 weeks

## 现有设备替换方案2 Replace Existing (hidden)
多肽厂房2现有设备替换-采购清单-只考虑现有设备及管道替换，不考虑其他（如新增CIP等） Peptide Building 2, replacement of existing equipment – purchasing list – covers replacement of existing equipment and piping only, excluding anything else (such as a new CIP system)
制备系统-连续配液-CNC区-设备清单 Preparation system – continuous solution preparation – CNC area – equipment list
序号 / No. | 设备位号 / Equipment tag | 设备名称 / Equipment name | 技术参数 / Technical parameters | 设备材质 / Equipment material | 使用介质 / Process medium | 单位 / Unit | 数量 / Quantity | 设备来源 / Equipment source | 采购周期（天） / Procurement lead time (days) | 安装周期 / Installation duration | 验证周期 / Qualification duration | 加3天清洗总计时间 / Total time including 3 days of cleaning | 技术要求 / Technical requirements |  | 暂按照10月20号左右设备到货后开始改造考虑，具体根据项目结束时间调整；下表中黄色填充部分到货时间需要采购进一步确认； Provisionally assumes that the retrofit starts after the equipment arrives around 20 October; to be adjusted according to the actual end of the production campaign. The delivery dates highlighted in yellow below still have to be confirmed by Purchasing.
1 | 1213-R05 | 哈氏合金反应釜 / Hastelloy reactor | 3000L哈氏合金釜 / 3000 L Hastelloy reactor | C276 | 浓盐溶液 / Concentrated salt solution | 台 / unit | 1 | N/A | 100 | 30 | 19d(打点2d，程序调试5d+泵调试3d+验证9d) 19 d (loop check 2 d, software commissioning 5 d + pump commissioning 3 d + qualification 9 d) 验证IQ与安装同步执行，打点结束后关闭IQ，IQ在程序调试阶段完成 IQ runs in parallel with installation; IQ is closed after the loop check and is completed during software commissioning | 52d | 1、设备应满足ASME BPE要求，包括不限于如下要求： 1. The equipment shall comply with ASME BPE, including but not limited to: （1）设备接口采用NA接口，满足2D要求；接口尺寸及数量以确认图纸为准； (1) NA-type connections meeting the 2D drainability requirement; connection sizes and quantities as per the approved drawings; （2）设计淋洗口，需配淋洗球，满足全面清洗且通过核黄素清洗验证； (2) Spray port with spray ball, giving full coverage and passing the riboflavin coverage test; （3）出料口焊接隔膜阀，满足2D要求； (3) Diaphragm valve welded to the outlet, meeting the 2D requirement; （4）外表面抛光粗糙度<0.8um，内壁抛光粗糙度<0.4um； (4) External surface roughness < 0.8 µm, internal surface roughness < 0.4 µm; (5) 设备的原材、配件、生产制造及验收应严格按照ASME BPE要求进行，并提供相关证明资料； (5) Raw materials, components, manufacturing and acceptance strictly in line with ASME BPE, with the supporting documentation provided; 2、电机、减速机要求： 2. Motor and gearbox: （1）采用国内知名品牌；整体外包不锈钢，满足卫生级要求； (1) Well-known domestic brand; fully stainless-steel clad to sanitary standard; （2）防爆等级 ExdIIBT4 Gb，防护等级不低于IP55;电机能效不低于二级； (2) Explosion protection Ex d IIB T4 Gb, ingress protection not lower than IP55; motor efficiency class 2 or better; 3、机封采用双端面卫生级干磨机封，采用国内知名品牌； 3. Double-end sanitary dry-running mechanical seal from a well-known domestic brand; 4、搅拌材质与罐体一直，搅拌形式最终确认图纸为准； 4. Agitator material identical to the vessel; agitator design as per the approved drawings; |  | 制备连续配液系统改造-3000LHC釜改口、更换8台罐（316L）、BPE管道 Retrofit of the continuous solution preparation system – rework of the 3000 L Hastelloy reactor nozzles, replacement of 8 vessels (316L), BPE piping
2 | 1211-HPPC03-AT01 | 配液搅拌罐（不带夹套） / Solution preparation agitated vessel (non-jacketed) | 有效容积500L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 500 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | C22或C276 / C22 or C276 | 浓盐溶液 / Concentrated salt solution | 台 / unit | 1 | N/A | —— | [5 empty] | 序号 / No. | 工序 / Activity | 设备/材料 / Equipment / material | 货期/工期 / Lead time / duration | 预计到货时间 / Expected delivery date | 10月 / October | [11 empty] | 11月 / November | [29 empty] | 12月 / December
3 | 1211-HPPC03-AT02 | 配液搅拌罐（不带夹套） / Solution preparation agitated vessel (non-jacketed) | 有效容积500L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 500 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | C22或C276 / C22 or C276 | 浓盐溶液 / Concentrated salt solution | 台 / unit | 1 | N/A | —— | [10 empty] | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 备注 / Remarks
4 | 1211-HPPC03-AT01 | 配液搅拌罐（不带夹套） / Solution preparation agitated vessel (non-jacketed) | 有效容积500L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 500 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 浓盐溶液 / Concentrated salt solution | 台 / unit | 1 | 利旧英德600L储罐（11）-改造6周（加搅拌、防爆电机、下口阀） Reuse Yingde 600 L storage tank (11) – 6-week modification (add agitator, explosion-proof motor, bottom outlet valve) | 42 | [5 empty] | 1 | 设备采购 / Equipment procurement | 3000L HC釜配件到货 / Delivery of the 3000 L Hastelloy reactor parts | 40 | 10月20 / 20 Oct | [49 empty] | 已订购 / Ordered | bar: 10月 / October 20
5 | 1211-HPPC03-AT02 | 配液搅拌罐（不带夹套） / Solution preparation agitated vessel (non-jacketed) | 有效容积500L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 500 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 浓盐溶液 / Concentrated salt solution | 台 / unit | 1 | 利旧英德600L储罐（11）-改造7周（加搅拌、防爆电机、下口阀） Reuse Yingde 600 L storage tank (11) – 7-week modification (add agitator, explosion-proof motor, bottom outlet valve) | 42 | [5 empty] | 2 |  | YD储罐到货（316） / Delivery of the YD storage tanks (316L) | 40 | 10月20 / 20 Oct | [49 empty] | 已订购 / Ordered | bar: 10月 / October 20
6 | 1211-HPPC03-T01 | 纯水储罐（不带夹套） / Purified water storage tank (non-jacketed) | 有效容积1000L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 1000 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 纯化水 / Purified water | 台 / unit | 1 | 利旧英德1000储罐（8）-改造6周，加下口阀 Reuse Yingde 1000 L storage tank (8) – 6-week modification, add bottom outlet valve | 42 |  |  |  | 设备应满足ASME BPE要求，包括不限于如下要求： The equipment shall comply with ASME BPE, including but not limited to: （1）设备接口采用NA接口，满足2D要求；接口尺寸及数量以确认图纸为准； (1) NA-type connections meeting the 2D drainability requirement; connection sizes and quantities as per the approved drawings; （2）设计淋洗口，需配淋洗球，满足全面清洗且通过核黄素清洗验证； (2) Spray port with spray ball, giving full coverage and passing the riboflavin coverage test; （3）出料口焊接隔膜阀，满足2D要求； (3) Diaphragm valve welded to the outlet, meeting the 2D requirement; （4）外表面抛光粗糙度<0.8um，内壁抛光粗糙度<0.4um； (4) External surface roughness < 0.8 µm, internal surface roughness < 0.4 µm; (5) 设备的原材、配件、生产制造及验收应严格按照ASME BPE要求进行，并提供相关证明资料； (5) Raw materials, components, manufacturing and acceptance strictly in line with ASME BPE, with the supporting documentation provided; |  | 3 |  | 离心泵到货（316） / Delivery of the centrifugal pumps (316L) | 42 | 10月25 / 25 Oct | [49 empty] | 未订购，预估到货时间 / Not ordered yet, estimated delivery date | bar: 10月 / October 20 to 10月 / October 25
7 | 1211-HPPC03-T02 | 乙腈储罐（不带夹套） / Acetonitrile storage tank (non-jacketed) | 有效容积1000L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 1000 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 新鲜乙腈、备用 / Fresh acetonitrile, spare | 台 / unit | 2 | 利旧英德1500储罐（12、13）-改造6周，加下口阀 Reuse Yingde 1500 L storage tanks (12, 13) – 6-week modification, add bottom outlet valve | 42 | [5 empty] | 4 |  | 四元隔膜泵到货（316） / Delivery of the four-head diaphragm pumps (316L) | 25 | 10月10 / 10 Oct | [49 empty] | 已订购 / Ordered | bar: 10月 / October 20
8 | 1211-HPPC03-T03 | 流动相A储罐（不带夹套） / Mobile phase A storage tank (non-jacketed) | 有效容积1000L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 1000 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 流动相A / Mobile phase A | 台 / unit | 1 | 利旧英德1000L储罐（9）-改造6周（改防爆电机、下口阀） Reuse Yingde 1000 L storage tank (9) – 6-week modification (change to explosion-proof motor, bottom outlet valve) | 42 | [5 empty] | 5 |  | 自控阀门/仪表采购（316） / Procurement of control valves / instruments (316L) | 42 | 10月25 / 25 Oct | [49 empty] | 部分已订购、部分未订购，预估到货时间 Partly ordered, partly not ordered; estimated delivery date | bar: 10月 / October 20 to 10月 / October 25
9 | 1211-HPPC03-T04 | 流动相B储罐（不带夹套） / Mobile phase B storage tank (non-jacketed) | 有效容积1000L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 1000 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 流动相B / Mobile phase B | 台 / unit | 1 | 利旧英德1000L储罐（10）-改造6周（改防爆电机、下口阀） Reuse Yingde 1000 L storage tank (10) – 6-week modification (change to explosion-proof motor, bottom outlet valve) | 42 | [5 empty] | 6 |  | BPE管件采购（316） / Procurement of BPE fittings (316L) | 30 | 10月15 / 15 Oct | [49 empty] | 已订购 / Ordered | bar: 10月 / October 20
10 | 1211-HPPC03-T05 | 甲醇储罐（不带夹套） / Methanol storage tank (non-jacketed) | 有效容积1000L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 1000 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 甲醇 / Methanol | 台 / unit | 1 | 1000储罐-改造6周，加下口阀。此罐计划取消 1000 L storage tank – 6-week modification, add bottom outlet valve. This tank is planned to be cancelled | 42 | [5 empty] | 7 |  | BPE手动阀门（316） / BPE manual valves (316L) | 30 | 10月15 / 15 Oct | [49 empty] | 已订购 / Ordered | bar: 10月 / October 20
11 | 1211-HPPC03-T03-P01 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：2.5m3/h 扬程：25m 卡箍连接 Rated flow 2.5 m³/h, head 25 m, clamp connection | SS316L | 流动相A / Mobile phase A | 台 / unit | 2 | 新采购 / Newly purchased | 45 |  |  |  | 设备应满足ASME BPE要求，包括不限于如下要求： The equipment shall comply with ASME BPE, including but not limited to: （1）设备接口采用NA接口，满足2D要求，设备腔体可排净； (1) NA-type connections meeting the 2D drainability requirement, with a fully drainable equipment body; （2）外表面抛光粗糙度<0.8um，内壁抛光粗糙度<0.4um； (2) External surface roughness < 0.8 µm, internal surface roughness < 0.4 µm; （3）设备的原材、配件、生产制造及验收应严格按照ASME BPE要求进行，并提供相关证明资料； (3) Raw materials, components, manufacturing and acceptance strictly in line with ASME BPE, with the supporting documentation provided; |  | 8 |  | BPE管件（HC） / BPE fittings (Hastelloy) | 60 | 11月10 / 10 Nov | [49 empty] | 已订购 / Ordered | bar: 10月 / October 20 to 11月 / November 10
12 | 1211-HPPC03-T03-P02 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：3.2m3/h 扬程：25m 卡箍连接 Rated flow 3.2 m³/h, head 25 m, clamp connection | SS316L | 流动相B / Mobile phase B | 台 / unit | 2 | 新采购 / Newly purchased | 45 | [5 empty] | 9 | 现场改造 / On-site modification | 3000LHC釜现场管口改造 / On-site nozzle modification of the 3000 L Hastelloy reactor | 10 | [50 empty] | 提前切割罐口 / Cut the vessel nozzles in advance | bar: 10月 / October 20 to 10月 / October 31
13 | 1211-HPPC03-T04-P01 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：2.5m3/h 扬程：25m 卡箍连接 Rated flow 2.5 m³/h, head 25 m, clamp connection | SS316L | 流动相B/新鲜乙腈 / Mobile phase B / fresh acetonitrile | 台 / unit | 2 | 新采购 / Newly purchased | 45 | [5 empty] | 10 |  | 3000LHC釜配管 / Piping of the 3000 L Hastelloy reactor | 4 | [50 empty] | 需要等HC件到货 / Waiting for delivery of the Hastelloy parts | bar: 11月 / November 11 to 11月 / November 14
14 | 1211-HPPC03-WT01-P01 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：3.2m3/h 扬程：20m 卡箍连接 Rated flow 3.2 m³/h, head 20 m, clamp connection | SS316L | 制备废液 / Preparation waste liquid | 台 / unit | 2 | 新采购 / Newly purchased | 45 | [5 empty] | 11 |  | 8台罐拆、装 / Removal and installation of 8 vessels | 3 | [50 empty] | 需要等储罐到货 / Waiting for delivery of the storage tanks | bar: 10月 / October 20 to 10月 / October 22
15 | 1211-HPPC03-WT02-P01 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：3.2m3/h 扬程：20m 卡箍连接 Rated flow 3.2 m³/h, head 20 m, clamp connection | SS316L | 制备废液 / Preparation waste liquid | 台 / unit | 2 | 新采购 / Newly purchased | 45 | [5 empty] | 12 |  | 泵及BPE管道更换 / Replacement of pumps and BPE piping | 20 | [50 empty] | —— | bar: 10月 / October 23 to 11月 / November 11
16 | 1211-HPPC03-AT01-P01 | 卫生级四元隔膜泵 / Sanitary four-head diaphragm pump | 额定流量：3.2m3/h 扬程：30m 卡箍连接 Rated flow 3.2 m³/h, head 30 m, clamp connection | C22或C276 / C22 or C276 | 浓盐溶液 / Concentrated salt solution | 台 / unit | 2 | 新采购 / Newly purchased | 45 | [5 empty] | 13 |  | 电气、仪表安装 / Electrical and instrumentation installation | 10 | [50 empty] | —— | bar: 11月 / November 3 to 11月 / November 12
17 | 1211-HPPC03-AT02-P01 | 卫生级四元隔膜泵 / Sanitary four-head diaphragm pump | 额定流量：3.2m3/h 扬程：30m 卡箍连接 Rated flow 3.2 m³/h, head 30 m, clamp connection | C22或C276 / C22 or C276 | 浓盐溶液 / Concentrated salt solution | 台 / unit | 2 | 新采购 / Newly purchased | 45 | [5 empty] | 14 |  | 地面施工、打胶 / Floor work and sealant application | 3 | [50 empty] | —— | bar: 11月 / November 13 to 11月 / November 15
18 | 1211-HPPC03-T01-P01 | 卫生级四元隔膜泵 / Sanitary four-head diaphragm pump | 额定流量：5m3/h 扬程：30m 卡箍连接 Rated flow 5 m³/h, head 30 m, clamp connection | SS316L | 纯化水 / Purified water | 台 / unit | 2 | 新采购 / Newly purchased | 45 | [5 empty] | 15 | 验证+清洗 / Qualification + cleaning | 验证IQ / IQ | [51 empty] | 验证IQ与安装同步执行，打点结束后关闭IQ，IQ在程序调试阶段完成 IQ runs in parallel with installation; IQ is closed after the loop check and is completed during software commissioning | bar: 11月 / November 14 to 11月 / November 17
19 | 1211-HPPC03-T01-P02 | 卫生级四元隔膜泵 / Sanitary four-head diaphragm pump | 额定流量：3.2m3/h 扬程：30m 卡箍连接 Rated flow 3.2 m³/h, head 30 m, clamp connection | SS316L | 纯化水 / Purified water | 台 / unit | 2 | 新采购 / Newly purchased | 45 | [5 empty] | 16 |  | 打点 / Loop check | [51 empty] | —— | bar: 11月 / November 16 to 11月 / November 17
20 | 1211-HPPC03-T02-P01 | 卫生级四元隔膜泵 / Sanitary four-head diaphragm pump | 额定流量：3.2m3/h 扬程：30m 卡箍连接 Rated flow 3.2 m³/h, head 30 m, clamp connection | SS316L | 新鲜乙腈 / Fresh acetonitrile | 台 / unit | 2 | 新采购 / Newly purchased | 45 | [5 empty] | 17 |  | 程序调试 / Software commissioning | [51 empty] | —— | bar: 11月 / November 18 to 11月 / November 22
21 | 1211-HPPC03-T02-P02 | 卫生级四元隔膜泵 / Sanitary four-head diaphragm pump | 额定流量：5m3/h 扬程：30m 卡箍连接 Rated flow 5 m³/h, head 30 m, clamp connection | SS316L | 新鲜乙腈 / Fresh acetonitrile | 台 / unit | 2 | 新采购 / Newly purchased | 45 | [5 empty] | 18 |  | 泵调试 / Pump commissioning | [51 empty] | —— | bar: 11月 / November 23 to 11月 / November 25
22 | 配件 / Components | 质量流量计（快开、BPE） / Mass flow meter (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 30 |  |  |  | BPE要求 / BPE requirements |  | 19 |  | 验证OPQ / OQ / PQ | [51 empty] | —— | bar: 11月 / November 26 to 12月 / December 7
23 |  | 气动隔膜调节阀（快开、BPE） Pneumatic diaphragm control valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 42
24 |  | 气动隔膜开关阀（快开、BPE） Pneumatic diaphragm on/off valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 42 | [5 empty] | 制备组分接收罐改造-6台储罐改2D接口、BPE管道 Retrofit of the fraction receiving vessels – conversion of 6 storage tanks to 2D connections, BPE piping
25 |  | 气动调节阀（快开、BPE） / Pneumatic control valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 42 | [5 empty] | 序号 / No. | 工序 / Activity | 设备/材料 / Equipment / material | 货期/工期 / Lead time / duration | 预计到货时间 / Expected delivery date | 10月 / October 20: 10月 / October; 11月 / November 1: 11月 / November; 12月 / December 1: 12月 / December
26 |  | 气动开关阀（快开、BPE） / Pneumatic on/off valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 42 | [10 empty] | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 备注 / Remarks
27 |  | 雷达液位计 / Radar level transmitter | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 20 | [5 empty] | 1 | 设备采购 / Equipment procurement | 储罐配件到货 / Delivery of the storage tank parts | 40 | 10月20 / 20 Oct | [49 empty] | 已订购 / Ordered | bar: 10月 / October 20
28 |  | 音叉 / Tuning-fork level switch | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 20 | [5 empty] | 2 |  | 离心泵到货（316） / Delivery of the centrifugal pumps (316L) | 42 | 10月25 / 25 Oct | [49 empty] | 未订购，预估到货时间 / Not ordered yet, estimated delivery date | bar: 10月 / October 20 to 10月 / October 25
29 |  | 温度 / Temperature instrument | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 20 | [5 empty] | 3 |  | 自控阀门/仪表采购（316） / Procurement of control valves / instruments (316L) | 42 | 10月25 / 25 Oct | [49 empty] | 部分已订购、部分未订购，预估到货时间 Partly ordered, partly not ordered; estimated delivery date | bar: 10月 / October 20 to 10月 / October 25
30 |  | PH / pH instrument | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 42 | [5 empty] | 4 |  | BPE管件采购（316） / Procurement of BPE fittings (316L) | 30 | 10月15 / 15 Oct | [49 empty] | 已订购 / Ordered | bar: 10月 / October 20
31 |  | 压力 / Pressure instrument | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 21 | [5 empty] | 5 |  | BPE手动阀门（316） / BPE manual valves (316L) | 30 | 10月15 / 15 Oct | [49 empty] | 已订购 / Ordered | bar: 10月 / October 20
32 |  | 手动隔膜阀 / Manual diaphragm valve | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 45 | [5 empty] | 6 | 现场改造 / On-site modification | 6台罐管口改造 / Nozzle modification of 6 vessels | 20 | [50 empty] | 管口比较多，且测口、下口改造涉及拆保温、夹套，很困难 There are many nozzles, and reworking the measurement and bottom nozzles means removing insulation and jackets, which is very difficult | bar: 10月 / October 21 to 11月 / November 9
33 |  | BPE管道、管件 / BPE piping and fittings | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 35 | [5 empty] | 7 |  | 泵及BPE管道更换 / Replacement of pumps and BPE piping | 15 | [50 empty] | —— | bar: 10月 / October 30 to 11月 / November 14
制备系统-D级区-设备清单 / Preparation system – Grade D area – equipment list | [14 empty] | 8 |  | 电气、仪表安装 / Electrical and instrumentation installation | 10 | [50 empty] | —— | bar: 11月 / November 6 to 11月 / November 15
序号 / No. | 设备位号 / Equipment tag | 设备名称 / Equipment name | 技术参数 / Technical parameters | 设备材质 / Equipment material | 使用介质 / Process medium | 单位 / Unit | 数量 / Quantity | 方案 / Option | 采购周期 / Procurement lead time | 安装周期 / Installation duration | 验证周期 / Qualification duration | 总计时间 / Total time | 技术要求 / Technical requirements |  | 9 |  | 地面施工、打胶处理 / Floor work and sealant treatment | 5 | [50 empty] | 施工面大，考虑地面重做 / Large working area; the floor is assumed to be redone | bar: 11月 / November 16 to 11月 / November 20
1 | 1211-HPPC03-AT03 | 组分接收搅拌罐（带夹套） / Fraction receiving agitated vessel (jacketed) | 1、有效容积8000L； 1. Working volume 8000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：316L不锈钢； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 设备不拆，改快开喇叭口（2D），采购配件 Equipment stays in place; convert to quick-connect flare (NA) nozzles, purchase the parts | 25 | 30 | 4d，24h 4 d, 24 h 验证IQ与安装同步执行，IQ1d；OQ3d IQ runs in parallel with installation; IQ 1 d, OQ 3 d | 37d | 1、设备应满足ASME BPE要求，包括不限于如下要求： 1. The equipment shall comply with ASME BPE, including but not limited to: （1）设备接口采用NA接口，满足2D要求；接口尺寸及数量以确认图纸为准； (1) NA-type connections meeting the 2D drainability requirement; connection sizes and quantities as per the approved drawings; （2）设计淋洗口，需配淋洗球，满足全面清洗且通过核黄素清洗验证； (2) Spray port with spray ball, giving full coverage and passing the riboflavin coverage test; （3）出料口焊接隔膜阀，满足2D要求； (3) Diaphragm valve welded to the outlet, meeting the 2D requirement; （4）外表面抛光粗糙度<0.8um，内壁抛光粗糙度<0.4um； (4) External surface roughness < 0.8 µm, internal surface roughness < 0.4 µm; (5) 设备的原材、配件、生产制造及验收应严格按照ASME BPE要求进行，并提供相关证明资料； (5) Raw materials, components, manufacturing and acceptance strictly in line with ASME BPE, with the supporting documentation provided; 2、电机、减速机要求： 2. Motor and gearbox: （1）采用国内知名品牌；整体外包不锈钢，满足卫生级要求； (1) Well-known domestic brand; fully stainless-steel clad to sanitary standard; （2）防爆等级 ExdIIBT4 Gb，防护等级不低于IP55;电机能效不低于二级； (2) Explosion protection Ex d IIB T4 Gb, ingress protection not lower than IP55; motor efficiency class 2 or better; 3、机封采用双端面卫生级干磨机封，采用国内知名品牌； 3. Double-end sanitary dry-running mechanical seal from a well-known domestic brand; 4、搅拌材质与罐体一直，搅拌形式最终确认图纸为准； 4. Agitator material identical to the vessel; agitator design as per the approved drawings; 5、保温厚度满足温度要求，外壳采用3mm不锈钢，外表抛光粗糙度<0.8um， 5. Insulation thickness to suit the temperature requirement; cladding in 3 mm stainless steel with an external surface roughness < 0.8 µm, |  | 10 | 验证+清洗 / Qualification + cleaning | IQ | [51 empty] | 验证IQ与安装同步执行 / IQ runs in parallel with installation | bar: 11月 / November 18 to 11月 / November 21
2 | 1211-HPPC03-AT04/AT05 | 组分接收搅拌罐（带夹套） / Fraction receiving agitated vessel (jacketed) | 1、有效容积3000L； 1. Working volume 3000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：316L不锈钢； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂等 / Various organic solvents | 台 / unit | 2 | 设备不拆，改快开喇叭口（2D），采购配件 Equipment stays in place; convert to quick-connect flare (NA) nozzles, purchase the parts | 25 | [5 empty] | 11 |  | OQ | bar: 11月 / November 22 to 11月 / November 27
3 | 1211-HPPC03-AT06 | 样品搅拌罐（带夹套） / Sample agitated vessel (jacketed) | 1、有效容积1000L； 1. Working volume 1000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：316L不锈钢； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 设备不拆，改快开喇叭口（2D），采购配件 Equipment stays in place; convert to quick-connect flare (NA) nozzles, purchase the parts | 25
4 | 1211-HPPC03-T06 | 顶样搅拌罐（带夹套） / Top-fraction sample agitated vessel (jacketed) | 1、有效容积1000L； 1. Working volume 1000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：316L不锈钢； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 设备不拆，改快开喇叭口（2D），采购配件 Equipment stays in place; convert to quick-connect flare (NA) nozzles, purchase the parts | 25
5 | *** | 组分接收储罐（不带夹套） / Fraction receiving storage tank (non-jacketed) | 有效容积100L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 100 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 12 | 确认新采购货期6-8周内到货，对整体影响不大 Confirmed that new units can be delivered within 6–8 weeks, with little impact on the overall schedule | ？ |  |  |  | 设备应满足ASME BPE要求，包括不限于如下要求： The equipment shall comply with ASME BPE, including but not limited to: （1）设备接口采用NA接口，满足2D要求；接口尺寸及数量以确认图纸为准； (1) NA-type connections meeting the 2D drainability requirement; connection sizes and quantities as per the approved drawings; （2）设计淋洗口，需配淋洗球，满足全面清洗且通过核黄素清洗验证； (2) Spray port with spray ball, giving full coverage and passing the riboflavin coverage test; （3）出料口焊接隔膜阀，满足2D要求； (3) Diaphragm valve welded to the outlet, meeting the 2D requirement; （4）外表面抛光粗糙度<0.8um，内壁抛光粗糙度<0.4um； (4) External surface roughness < 0.8 µm, internal surface roughness < 0.4 µm; (5) 设备的原材、配件、生产制造及验收应严格按照ASME BPE要求进行，并提供相关证明资料； (5) Raw materials, components, manufacturing and acceptance strictly in line with ASME BPE, with the supporting documentation provided;
6 | *** | 气动隔膜泵 / Pneumatic diaphragm pump | 5m³/h，25m，快开连接 / 5 m³/h, 25 m, quick-connect | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 10 | 购新安装 / Purchase new and install | 15 |  |  |  | 设备应满足ASME BPE要求，包括不限于如下要求： The equipment shall comply with ASME BPE, including but not limited to: （1）设备接口采用NA接口，满足2D要求，设备腔体可排净； (1) NA-type connections meeting the 2D drainability requirement, with a fully drainable equipment body; （2）外表面抛光粗糙度<0.8um，内壁抛光粗糙度<0.4um； (2) External surface roughness < 0.8 µm, internal surface roughness < 0.4 µm; （3）设备的原材、配件、生产制造及验收应严格按照ASME BPE要求进行，并提供相关证明资料； (3) Raw materials, components, manufacturing and acceptance strictly in line with ASME BPE, with the supporting documentation provided;
21 | 配件 / Components | 质量流量计（快开、BPE） / Mass flow meter (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 30 | [5 empty] | 超滤区改造-更换1台储罐（316L）、BPE管道 Retrofit of the ultrafiltration area – replacement of 1 storage tank (316L), BPE piping
22 |  | 气动隔膜调节阀（快开、BPE） Pneumatic diaphragm control valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 42 | [5 empty] | 序号 / No. | 工序 / Activity | 设备/材料 / Equipment / material | 货期/工期 / Lead time / duration | 预计到货时间 / Expected delivery date | 10月 / October 20: 10月 / October; 11月 / November 1: 11月 / November; 12月 / December 1: 12月 / December
23 |  | 气动隔膜开关阀（快开、BPE） Pneumatic diaphragm on/off valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 42 | [10 empty] | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 备注 / Remarks
24 |  | 气动调节阀（快开、BPE） / Pneumatic control valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 42 | [5 empty] | 1 | 设备采购 / Equipment procurement | YD储罐到货（316） / Delivery of the YD storage tanks (316L) | 40 | 10月20 / 20 Oct | [49 empty] | 已订购 / Ordered | bar: 10月 / October 20
25 |  | 气动开关阀（快开、BPE） / Pneumatic on/off valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 42 | [5 empty] | 2 |  | 自控阀门/仪表采购（316） / Procurement of control valves / instruments (316L) | 42 | 10月25 / 25 Oct | [49 empty] | 部分已订购、部分未订购，预估到货时间 Partly ordered, partly not ordered; estimated delivery date | bar: 10月 / October 20 to 10月 / October 25
26 |  | 雷达液位计 / Radar level transmitter | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 20 | [5 empty] | 3 |  | BPE管件采购（316） / Procurement of BPE fittings (316L) | 30 | 10月15 / 15 Oct | [49 empty] | 已订购 / Ordered | bar: 10月 / October 20
27 |  | 音叉 / Tuning-fork level switch | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 20 | [5 empty] | 4 |  | BPE手动阀门（316） / BPE manual valves (316L) | 30 | 10月15 / 15 Oct | [49 empty] | 已订购 / Ordered | bar: 10月 / October 20
28 |  | 温度 / Temperature instrument | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 20 | [5 empty] | 5 | 现场改造 / On-site modification | 彩钢板拆除、 / Removal of sandwich panels, | 1 | [50 empty] | 提前拆除 / Remove in advance | bar: 10月 / October 20
29 |  | PH / pH instrument | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 42 | [5 empty] | 6 |  | 储罐拆、装 / Removal and installation of the storage tank | 1 | [50 empty] | —— | bar: 10月 / October 21
30 |  | 压力 / Pressure instrument | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 21 | [5 empty] | 7 |  | BPE管道更换 / Replacement of BPE piping | 5 | [50 empty] | —— | bar: 10月 / October 22 to 10月 / October 26
31 |  | 手动隔膜阀 / Manual diaphragm valve | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 45 | [5 empty] | 8 |  | 电气、仪表安装 / Electrical and instrumentation installation | 3 | [50 empty] | —— | bar: 10月 / October 24 to 10月 / October 26
32 |  | BPE管道、管件 / BPE piping and fittings | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 35 | [5 empty] | 9 |  | 地面施工、打胶处理 / Floor work and sealant treatment | 5 | [50 empty] | 更换设备，考虑地面重做 / Equipment replacement; the floor is assumed to be redone | bar: 10月 / October 27 to 10月 / October 31
超滤系统设备清单 / Ultrafiltration system equipment list | [14 empty] | 10 | 验证+清洗 / Qualification + cleaning | 调试 / Commissioning | bar: 11月 / November 1
序号 / No. | 设备位号 / Equipment tag | 设备名称 / Equipment name | 技术参数 / Technical parameters | 设备材质 / Equipment material | 使用介质 / Process medium | 单位 / Unit | 数量 / Quantity | 方案 / Option | 采购周期 / Procurement lead time | 安装周期 / Installation duration | 验证周期 / Qualification duration | 总计时间 / Total time | 技术要求 / Technical requirements |  | 11 |  | IQ | [51 empty] | 验证IQ与安装同步执行 / IQ runs in parallel with installation | bar: 10月 / October 29 to 11月 / November 1
1 | 1211-TFF01-T01 | 超滤接收储罐（带夹套） / Ultrafiltration receiving storage tank (jacketed) | 1、有效容积1000L； 1. Working volume 1000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 利旧英德1500L储罐（7）-改造6周（改防爆电机、下口阀） Reuse Yingde 1500 L storage tank (7) – 6-week modification (change to explosion-proof motor, bottom outlet valve) | 42 | 10 | 6d，24h 6 d, 24 h 验证IQ与安装同步执行，IQ在调试阶段关闭；调试1d，EOQ+OQ3d，PQ2d IQ runs in parallel with installation and is closed during commissioning; commissioning 1 d, EOQ + OQ 3 d, PQ 2 d | 19d | 设备应满足ASME BPE要求，包括不限于如下要求： The equipment shall comply with ASME BPE, including but not limited to: （1）设备接口采用NA接口，满足2D要求；接口尺寸及数量以确认图纸为准； (1) NA-type connections meeting the 2D drainability requirement; connection sizes and quantities as per the approved drawings; （2）设计淋洗口，需配淋洗球，满足全面清洗且通过核黄素清洗验证； (2) Spray port with spray ball, giving full coverage and passing the riboflavin coverage test; （3）出料口焊接隔膜阀，满足2D要求； (3) Diaphragm valve welded to the outlet, meeting the 2D requirement; （4）外表面抛光粗糙度<0.8um，内壁抛光粗糙度<0.4um； (4) External surface roughness < 0.8 µm, internal surface roughness < 0.4 µm; (5) 设备的原材、配件、生产制造及验收应严格按照ASME BPE要求进行，并提供相关证明资料； (5) Raw materials, components, manufacturing and acceptance strictly in line with ASME BPE, with the supporting documentation provided; |  | 12 |  | OPQ | bar: 11月 / November 2 to 11月 / November 9
2 | 配件 / Components | 质量流量计（快开、BPE） / Mass flow meter (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 30
3 |  | 气动隔膜调节阀（快开、BPE） Pneumatic diaphragm control valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 42
4 |  | 气动隔膜开关阀（快开、BPE） Pneumatic diaphragm on/off valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 42
5 |  | 手动隔膜阀 / Manual diaphragm valve | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 45
6 |  | BPE管道、管件 / BPE piping and fittings | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 35 | [5 empty] | 沉淀区改造-更换2000LHC釜、三合一（HC）、600L储罐、80L储罐、BPE管道 Retrofit of the precipitation area – replacement of the 2000 L Hastelloy reactor, filter-dryer (Hastelloy), 600 L storage tank, 80 L storage tank, BPE piping
沉淀釜区设备清单 / Precipitation reactor area equipment list | [14 empty] | 序号 / No. | 工序 / Activity | 设备/材料 / Equipment / material | 货期/工期 / Lead time / duration | 预计到货时间 / Expected delivery date | 10月 / October 20: 12月 / December; 11月 / November 6: 01月 / January; 12月 / December 7: 2月 / February
序号 / No. | 设备位号 / Equipment tag | 设备名称 / Equipment name | 技术参数 / Technical parameters | 设备材质 / Equipment material | 使用介质 / Process medium | 单位 / Unit | 数量 / Quantity | 方案 / Option | 采购周期 / Procurement lead time | 安装周期 / Installation duration | 验证周期 / Qualification duration | 总计时间 / Total time | 技术要求 / Technical requirements | [6 empty] | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 1 | 备注 / Remarks
1 | 1211-R01 | 析晶釜 / Crystallizer | 1、有效容积2000L； 1. Working volume 2000 L; 2、釜内设计温度-25~200℃，夹套设计温度-25~220℃； 2. Reactor design temperature −25 to 200 °C, jacket design temperature −25 to 220 °C; 3、釜内设计压力-0.1~0.4MPa；夹套工作压力0.6Mpa； 3. Reactor design pressure −0.1 to 0.4 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：304不锈钢衬C22或C276； Product contact: 304 stainless steel lined with C22 or C276; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、酸、碱等 / Various organic solvents, acids, bases, etc. | 台 / unit | 1 | 购新安装 / Purchase new and install | 100 | 30 | 18d（验证18d，）24h 18 d (qualification 18 d), 24 h 反应釜/三合一 Reactor / filter-dryer 需要重新验证 Requalification required 调试1d，空调EOQ+OQ5d，PQ12d，死时间 Commissioning 1 d, HVAC EOQ + OQ 5 d, PQ 12 d, dead time | 51d | 1、设备应满足ASME BPE要求，包括不限于如下要求： 1. The equipment shall comply with ASME BPE, including but not limited to: （1）设备接口采用NA接口，满足2D要求；接口尺寸及数量以确认图纸为准； (1) NA-type connections meeting the 2D drainability requirement; connection sizes and quantities as per the approved drawings; （2）设计淋洗口，需配淋洗球，满足全面清洗且通过核黄素清洗验证； (2) Spray port with spray ball, giving full coverage and passing the riboflavin coverage test; （3）出料口焊接隔膜阀，满足2D要求； (3) Diaphragm valve welded to the outlet, meeting the 2D requirement; （4）外表面抛光粗糙度<0.8um，内壁抛光粗糙度<0.4um； (4) External surface roughness < 0.8 µm, internal surface roughness < 0.4 µm; (5) 设备的原材、配件、生产制造及验收应严格按照ASME BPE要求进行，并提供相关证明资料； (5) Raw materials, components, manufacturing and acceptance strictly in line with ASME BPE, with the supporting documentation provided; 2、电机、减速机要求： 2. Motor and gearbox: （1）采用国内知名品牌；整体外包不锈钢，满足卫生级要求； (1) Well-known domestic brand; fully stainless-steel clad to sanitary standard; （2）防爆等级 ExdIIBT4 Gb，防护等级不低于IP55;电机能效不低于二级； (2) Explosion protection Ex d IIB T4 Gb, ingress protection not lower than IP55; motor efficiency class 2 or better; 3、机封采用双端面卫生级干磨机封，采用国内知名品牌； 3. Double-end sanitary dry-running mechanical seal from a well-known domestic brand; 4、搅拌材质与罐体一直，搅拌形式最终确认图纸为准； 4. Agitator material identical to the vessel; agitator design as per the approved drawings; 5、保温厚度满足温度要求，外壳采用3mm不锈钢，外表抛光粗糙度<0.8um， 5. Insulation thickness to suit the temperature requirement; cladding in 3 mm stainless steel with an external surface roughness < 0.8 µm, |  | 1 | 设备采购 / Equipment procurement | 2000LHC釜到货 / Delivery of the 2000 L Hastelloy reactor | 100 | 12月25 / 25 Dec | [49 empty] | 已订购 / Ordered | bar: 12月 / December 15 to 12月 / December 23
2 | 1211-R01 | 析晶釜 / Crystallizer | 1、有效容积2000L； 1. Working volume 2000 L; 2、釜内设计温度-25~200℃，夹套设计温度-25~220℃； 2. Reactor design temperature −25 to 200 °C, jacket design temperature −25 to 220 °C; 3、釜内设计压力-0.1~0.4MPa；夹套工作压力0.6Mpa； 3. Reactor design pressure −0.1 to 0.4 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：SS316L； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、酸、碱等 / Various organic solvents, acids, bases, etc. | 台 / unit | 1 | 购新安装 / Purchase new and install | 100 | [5 empty] | 2 |  | DN1200三合一到货 / Delivery of the DN1200 filter-dryer | 100 | 12月25 / 25 Dec | [49 empty] | 已订购 / Ordered | bar: 12月 / December 15 to 12月 / December 23
3 | 1211-AT01 | 搅拌罐 / Agitated vessel | 1、有效容积600L； 1. Working volume 600 L; 2、罐内设计温度-25~200℃，夹套设计温度-25~220℃； 2. Vessel design temperature −25 to 200 °C, jacket design temperature −25 to 220 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：316L不锈钢； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、盐溶液等 / Various organic solvents, salt solutions, etc. | 台 / unit | 1 | 购新安装 / Purchase new and install | 75 | [5 empty] | 3 |  | 储罐到货（316） / Delivery of the storage tanks (316L) | 90 | 12月15 / 15 Dec | [49 empty] | 未订购，预估到货时间 / Not ordered yet, estimated delivery date | bar: 12月 / December 15
4 | 1211-AT02 | 搅拌罐 / Agitated vessel | 1、有效容积80L； 1. Working volume 80 L; 2、罐内设计温度-25~200℃，夹套设计温度-25~220℃； 2. Vessel design temperature −25 to 200 °C, jacket design temperature −25 to 220 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：316L不锈钢； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、酸、碱等 / Various organic solvents, acids, bases, etc. | 台 / unit | 1 | 利旧英德600L储罐（6）-改造6周（双端面机封、防爆电机、下口阀） Reuse Yingde 600 L storage tank (6) – 6-week modification (double-end mechanical seal, explosion-proof motor, bottom outlet valve) | 75 | [5 empty] | 4 |  | 离心泵到货（316） / Delivery of the centrifugal pumps (316L) | 42 | 10月25 / 25 Oct | [49 empty] | 未订购，预估到货时间 / Not ordered yet, estimated delivery date
5 | 1211-Fd01 | 三合一 / Filter-dryer | 1、设备尺寸DN1200； 1. Equipment size DN1200; 2、罐内设计温度-25~200℃，夹套设计温度-25~220℃； 2. Vessel design temperature −25 to 200 °C, jacket design temperature −25 to 220 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：304不锈钢衬C22或C276； Product contact: 304 stainless steel lined with C22 or C276; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、酸、碱等 / Various organic solvents, acids, bases, etc. | 台 / unit | 1 | 购新安装 / Purchase new and install | 120 |  |  |  | 1、设备应满足ASME BPE要求，包括不限于如下要求： 1. The equipment shall comply with ASME BPE, including but not limited to: （1）设备接口采用NA接口，满足2D要求；接口尺寸及数量以确认图纸为准； (1) NA-type connections meeting the 2D drainability requirement; connection sizes and quantities as per the approved drawings; （2）设计淋洗口，需配淋洗球，满足全面清洗且通过核黄素清洗验证； (2) Spray port with spray ball, giving full coverage and passing the riboflavin coverage test; （3）出料口焊接隔膜阀，满足2D要求； (3) Diaphragm valve welded to the outlet, meeting the 2D requirement; （4）外表面抛光粗糙度<0.8um，内壁抛光粗糙度<0.4um； (4) External surface roughness < 0.8 µm, internal surface roughness < 0.4 µm; (5) 设备的原材、配件、生产制造及验收应严格按照ASME BPE要求进行，并提供相关证明资料； (5) Raw materials, components, manufacturing and acceptance strictly in line with ASME BPE, with the supporting documentation provided; 2、电机、减速机要求： 2. Motor and gearbox: （1）采用国内知名品牌；整体外包不锈钢，满足卫生级要求； (1) Well-known domestic brand; fully stainless-steel clad to sanitary standard; （2）防爆等级 ExdIIBT4 Gb，防护等级不低于IP55;电机能效不低于二级； (2) Explosion protection Ex d IIB T4 Gb, ingress protection not lower than IP55; motor efficiency class 2 or better; 3、机封采用双端面卫生级干磨机封，采用进口知名品牌，如约翰克兰、伯格曼； 3. Double-end sanitary dry-running mechanical seal from a well-known imported brand such as John Crane or Burgmann; 4、搅拌材质与罐体一直，搅拌形式最终确认图纸为准； 4. Agitator material identical to the vessel; agitator design as per the approved drawings; 5、保温厚度满足温度要求，外壳采用3mm不锈钢，外表抛光粗糙度<0.8um， 5. Insulation thickness to suit the temperature requirement; cladding in 3 mm stainless steel with an external surface roughness < 0.8 µm, |  | 5 |  | 自控阀门/仪表采购（316） / Procurement of control valves / instruments (316L) | 42 | 10月25 / 25 Oct | [49 empty] | 部分已订购、部分未订购，预估到货时间 Partly ordered, partly not ordered; estimated delivery date
6 | 1211-Fd01 | 三合一 / Filter-dryer | 1、设备尺寸DN1200； 1. Equipment size DN1200; 2、罐内设计温度-25~200℃，夹套设计温度-25~220℃； 2. Vessel design temperature −25 to 200 °C, jacket design temperature −25 to 220 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：SS316L； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、酸、碱等 / Various organic solvents, acids, bases, etc. | 台 / unit | 1 | 购新安装 / Purchase new and install | 120 | [5 empty] | 6 |  | BPE管件采购（316） / Procurement of BPE fittings (316L) | 30 | 10月15 / 15 Oct | [49 empty] | 已订购 / Ordered
7 | *** | 旋分筛 / Rotary sifter | 处理量200kg/h. Throughput 200 kg/h. | SS316L | 固体 / Solids | 台 / unit | 1 | 购新安装 / Purchase new and install | ？ |  |  |  | 1、设备应满足ASME BPE要求，包括不限于如下要求： 1. The equipment shall comply with ASME BPE, including but not limited to: （1）外表面抛光粗糙度<0.8um，内壁抛光粗糙度<0.4um； (1) External surface roughness < 0.8 µm, internal surface roughness < 0.4 µm; (2) 设备的原材、配件、生产制造及验收应严格按照ASME BPE要求进行，并提供相关证明资料； (2) Raw materials, components, manufacturing and acceptance strictly in line with ASME BPE, with the supporting documentation provided; | 生产确认需求 / Requirement to be confirmed by Production | 7 |  | BPE手动阀门（316） / BPE manual valves (316L) | 30 | 10月15 / 15 Oct | [49 empty] | 已订购 / Ordered
8 | 配件 / Components | 质量流量计（快开、BPE） / Mass flow meter (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 30 | [5 empty] | 8 |  | BPE管件（HC） / BPE fittings (Hastelloy) | 60 | 11月30 / 30 Nov | [49 empty] | 已订购 / Ordered
9 |  | 气动隔膜调节阀（快开、BPE） Pneumatic diaphragm control valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 42 | [5 empty] | 9 | 现场改造 / On-site modification | 管道、电气、彩板拆除 / Removal of piping, electrics and sandwich panels | 4 | [50 empty] | 设备到货前提前1周拆除 / Remove one week before the equipment arrives | bar: 12月 / December 15 to 12月 / December 18
10 |  | 气动隔膜开关阀（快开、BPE） Pneumatic diaphragm on/off valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 42 | [5 empty] | 10 |  | 钢平台拆除 / Removal of the steel platform | 2 | bar: 12月 / December 19 to 12月 / December 20
11 |  | 手动隔膜阀 / Manual diaphragm valve | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 45 | [5 empty] | 11 |  | 外墙拆除 / Removal of the external wall | 1 | bar: 12月 / December 21
12 |  | BPE管道、管件 / BPE piping and fittings | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 35 | [5 empty] | 12 |  | 设备拆除 / Equipment removal | 1 | bar: 12月 / December 22
[15 empty] | 13 |  | 设备吊装、组装 / Equipment lifting and assembly | 2 | [50 empty] | —— | bar: 12月 / December 23 to 12月 / December 24
[15 empty] | 14 |  | 钢平台恢复、外墙恢复 / Reinstatement of the steel platform and the external wall | 5 | [50 empty] | —— | bar: 12月 / December 25 to 12月 / December 29
[15 empty] | 15 |  | 彩钢板恢复 / Reinstatement of the sandwich panels | 5 | [50 empty] | —— | bar: 12月 / December 25 to 12月 / December 29
[15 empty] | 16 |  | 设备管道安装 / Installation of equipment and piping | 10 | [50 empty] | —— | bar: 12月 / December 28 to 01月 / January 6
[15 empty] | 17 |  | 电气、仪表安装 / Electrical and instrumentation installation | 5 | [50 empty] | —— | bar: 01月 / January 3 to 01月 / January 7
[15 empty] | 18 |  | 地面施工、打胶处理 / Floor work and sealant treatment | 7 | [50 empty] | 破坏面积大，需要重新做地面，细节处理等 Large damaged area; the floor has to be redone, including detail work | bar: 01月 / January 8 to 01月 / January 14
[15 empty] | 19 | 验证 / Qualification | 空调调试+opq / HVAC commissioning + OQ / PQ | bar: 01月 / January 15 to 2月 / February 1

## 新批次方案1全部新购 New System (hidden)
多肽厂房2新做批次配液系统-设备采购清单--按PID图安装 Peptide Building 2, new batch solution preparation system – equipment purchasing list – installed according to the P&ID
制备配液系统设备清单 / Preparation / solution system equipment list
序号 / No. | 设备位号 / Equipment tag | 设备名称 / Equipment name | 技术参数 / Technical parameters | 设备材质 / Equipment material | 使用介质 / Process medium | 单位 / Unit | 数量 / Quantity | 设备来源 / Equipment source | 采购周期 / Procurement lead time | 安装周期 / Installation duration | 验证周期 / Qualification duration | 总计时间 / Total time | 技术要求 / Technical requirements
1 | *** | 配盐搅拌罐（带夹套） / Salt solution agitated vessel (jacketed) | 1、有效容积3000L； 1. Working volume 3000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：304不锈钢衬C22或C276； Product contact: 304 stainless steel lined with C22 or C276; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、酸、碱等 / Various organic solvents, acids, bases, etc. | 台 / unit | 2 | 新采购 / Newly purchased | 100 | 23 | 1、工程打点3d，调试和验证共15d(程序调试4d+泵调试3d+验证8d：OQ4d、程序EOQ2d，PQ2d) 1. Engineering loop check 3 d; commissioning and qualification 15 d in total (software commissioning 4 d + pump commissioning 3 d + qualification 8 d: OQ 4 d, software EOQ 2 d, PQ 2 d) 2、影响制备区域的环境（涉及穿墙管焊接），需要重新做相应的微生物检测，和配液系统同步，不影响整体放行的时间 2. The environment of the preparation area is affected (wall penetration welding is involved), so the corresponding microbial monitoring has to be repeated in parallel with the solution system; this does not affect the overall release date 3、CNC区域的空调重新OQ，不影响整体的放行时间 3. The HVAC of the CNC area has to be re-qualified (OQ); this does not affect the overall release date |  | 1、设备应满足ASME BPE要求，包括不限于如下要求： 1. The equipment shall comply with ASME BPE, including but not limited to: （1）设备接口采用NA接口，满足2D要求；接口尺寸及数量以确认图纸为准； (1) NA-type connections meeting the 2D drainability requirement; connection sizes and quantities as per the approved drawings; （2）设计淋洗口，需配淋洗球，满足全面清洗且通过核黄素清洗验证； (2) Spray port with spray ball, giving full coverage and passing the riboflavin coverage test; （3）出料口焊接隔膜阀，满足2D要求； (3) Diaphragm valve welded to the outlet, meeting the 2D requirement; （4）外表面抛光粗糙度<0.8um，内壁抛光粗糙度<0.4um； (4) External surface roughness < 0.8 µm, internal surface roughness < 0.4 µm; (5) 设备的原材、配件、生产制造及验收应严格按照ASME BPE要求进行，并提供相关证明资料； (5) Raw materials, components, manufacturing and acceptance strictly in line with ASME BPE, with the supporting documentation provided; 2、电机、减速机要求： 2. Motor and gearbox: （1）采用国内知名品牌；整体外包不锈钢，满足卫生级要求； (1) Well-known domestic brand; fully stainless-steel clad to sanitary standard; （2）防爆等级 ExdIIBT4 Gb，防护等级不低于IP55;电机能效不低于二级； (2) Explosion protection Ex d IIB T4 Gb, ingress protection not lower than IP55; motor efficiency class 2 or better; 3、机封采用双端面卫生级干磨机封，采用国内知名品牌； 3. Double-end sanitary dry-running mechanical seal from a well-known domestic brand; 4、搅拌材质与罐体一直，搅拌形式最终确认图纸为准； 4. Agitator material identical to the vessel; agitator design as per the approved drawings; 5、保温厚度满足温度要求，外壳采用3mm不锈钢，外表抛光粗糙度<0.8um， 5. Insulation thickness to suit the temperature requirement; cladding in 3 mm stainless steel with an external surface roughness < 0.8 µm,
2 | *** | 配盐搅拌罐（带夹套） / Salt solution agitated vessel (jacketed) | 1、有效容积3000L； 1. Working volume 3000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：SS316L； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、酸、碱等 / Various organic solvents, acids, bases, etc. | 台 / unit | 2 | 新采购 / Newly purchased | 75
3 | *** | 流动相A搅拌罐（带夹套） / Mobile phase A agitated vessel (jacketed) | 1、有效容积3000L； 1. Working volume 3000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：SS316L； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、酸、碱等 / Various organic solvents, acids, bases, etc. | 台 / unit | 2 | 新采购 / Newly purchased | 75
4 | *** | 流动相B搅拌罐（带夹套） / Mobile phase B agitated vessel (jacketed) | 1、有效容积3000L； 1. Working volume 3000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：SS316L； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、酸、碱等 / Various organic solvents, acids, bases, etc. | 台 / unit | 3 | 新采购 / Newly purchased | 75
5 | *** | 乙腈储罐（不带夹套） / Acetonitrile storage tank (non-jacketed) | 有效容积1000L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 1000 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 新鲜乙腈 / Fresh acetonitrile | 台 / unit | 2 | 新采购 / Newly purchased | 75 |  |  |  | 设备应满足ASME BPE要求，包括不限于如下要求： The equipment shall comply with ASME BPE, including but not limited to: （1）设备接口采用NA接口，满足2D要求；接口尺寸及数量以确认图纸为准； (1) NA-type connections meeting the 2D drainability requirement; connection sizes and quantities as per the approved drawings; （2）设计淋洗口，需配淋洗球，满足全面清洗且通过核黄素清洗验证； (2) Spray port with spray ball, giving full coverage and passing the riboflavin coverage test; （3）出料口焊接隔膜阀，满足2D要求； (3) Diaphragm valve welded to the outlet, meeting the 2D requirement; （4）外表面抛光粗糙度<0.8um，内壁抛光粗糙度<0.4um； (4) External surface roughness < 0.8 µm, internal surface roughness < 0.4 µm; (5) 设备的原材、配件、生产制造及验收应严格按照ASME BPE要求进行，并提供相关证明资料； (5) Raw materials, components, manufacturing and acceptance strictly in line with ASME BPE, with the supporting documentation provided;
6 | *** | 甲醇储罐（不带夹套） / Methanol storage tank (non-jacketed) | 有效容积1000L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 1000 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 新鲜甲醇 / Fresh methanol | 台 / unit | 1 | 新采购 / Newly purchased | 75
7 | *** | 纯化水储罐（不带夹套） / Purified water storage tank (non-jacketed) | 有效容积1000L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 1000 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 纯换水 / Purified water | 台 / unit | 1 | 新采购 / Newly purchased | 75
8 | *** | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：12.5m3/h 扬程：25m 卡箍连接 Rated flow 12.5 m³/h, head 25 m, clamp connection | C22或C276 / C22 or C276 | 浓盐溶液 / Concentrated salt solution | 台 / unit | 2 | 新采购 / Newly purchased | 45 |  |  |  | 设备应满足ASME BPE要求，包括不限于如下要求： The equipment shall comply with ASME BPE, including but not limited to: （1）设备接口采用NA接口，满足2D要求，设备腔体可排净； (1) NA-type connections meeting the 2D drainability requirement, with a fully drainable equipment body; （2）外表面抛光粗糙度<0.8um，内壁抛光粗糙度<0.4um； (2) External surface roughness < 0.8 µm, internal surface roughness < 0.4 µm; （3）设备的原材、配件、生产制造及验收应严格按照ASME BPE要求进行，并提供相关证明资料； (3) Raw materials, components, manufacturing and acceptance strictly in line with ASME BPE, with the supporting documentation provided;
9 | *** | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：12.5m3/h 扬程：25m 卡箍连接 Rated flow 12.5 m³/h, head 25 m, clamp connection | SS316L | 流动相A / Mobile phase A | 台 / unit | 3 | 新采购 / Newly purchased | 45
10 | *** | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：12.5m3/h 扬程：25m 卡箍连接 Rated flow 12.5 m³/h, head 25 m, clamp connection | SS316L | 流动相B / Mobile phase B | 台 / unit | 3 | 新采购 / Newly purchased | 45
11 | *** | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：12.5m3/h 扬程：25m 卡箍连接 Rated flow 12.5 m³/h, head 25 m, clamp connection | SS316L | 纯化水 / Purified water | 台 / unit | 2 | 新采购 / Newly purchased | 45
12 | *** | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：3.2m3/h 扬程：25m 卡箍连接 Rated flow 3.2 m³/h, head 25 m, clamp connection | SS316L | 乙腈 / Acetonitrile | 台 / unit | 2 | 新采购 / Newly purchased | 45
13 | *** | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：5m3/h 扬程：30m 卡箍连接 Rated flow 5 m³/h, head 30 m, clamp connection | SS316L | 甲醇 / Methanol | 台 / unit | 3 | 新采购 / Newly purchased | 45
14 | *** | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：5m3/h 扬程：30m 卡箍连接 Rated flow 5 m³/h, head 30 m, clamp connection | SS316L | 废液 / Waste liquid | 台 / unit | 2 | 新采购 / Newly purchased | 45
21 | 配件 / Components | 质量流量计（快开、BPE） / Mass flow meter (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 30 |  |  |  | BPE要求 / BPE requirements
22 |  | 气动隔膜调节阀（快开、BPE） Pneumatic diaphragm control valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 42
23 |  | 气动隔膜开关阀（快开、BPE） Pneumatic diaphragm on/off valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 42
24 |  | 气动调节阀（快开、BPE） / Pneumatic control valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 42
25 |  | 气动开关阀（快开、BPE） / Pneumatic on/off valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 42
26 |  | 雷达液位计 / Radar level transmitter | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 20
27 |  | 音叉 / Tuning-fork level switch | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 20
28 |  | 温度 / Temperature instrument | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 20
29 |  | PH / pH instrument | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 42
30 |  | 压力 / Pressure instrument | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 21
31 |  | 手动隔膜阀 / Manual diaphragm valve | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 45
32 |  | BPE管道、管件 / BPE piping and fittings | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 35

## 方案1 Option 1 Retrofit Only (hidden)
多肽厂房2现有设备替换-采购清单-只考虑现状改造满足客户最新会议需求，约11/30/2026完成 Peptide Building 2, replacement of existing equipment – purchasing list – covers only the modification of the existing installation to meet the latest customer meeting requirements, completion around 30 Nov 2026
制备系统-连续配液-CNC区-设备清单-客户需求 Preparation system – continuous solution preparation – CNC area – equipment list – customer requirements | [14 empty] | 按照10月15号左右生产结束开始改造； Assumes the retrofit starts when production finishes, around 15 October; | [47 empty] | 按照10月15号左右生产结束开始改造； Assumes the retrofit starts when production finishes, around 15 October;
序号 / No. | 设备位号 / Equipment tag | 设备名称 / Equipment name | 技术参数 / Technical parameters | 设备材质 / Equipment material | 使用介质 / Process medium | 单位 / Unit | 数量 / Quantity | 设备来源 / Equipment source | 改造需求 / Modification requirement | 采购周期（天） / Procurement lead time (days) | 09/17目前进展 / Status as of 09/17 | 改造周期 / Modification duration | 验证周期 / Qualification duration | 加3天清洗总计时间 / Total time including 3 days of cleaning | 制备连续配液系统改造-3000LHC釜改TC口、2台浓盐罐更换YD储罐（316L）、BPE管道（316L）-问题：现场储罐为自行改造的TC口，需要征求客户意见；浓盐管道需要评估316L能否满足？ Retrofit of the continuous solution preparation system – convert the 3000 L Hastelloy reactor to TC connections, replace the 2 concentrated-salt vessels with YD storage tanks (316L), BPE piping (316L). Open points: the TC connections on the existing site tanks were made in-house, so the customer's opinion is needed; it must be assessed whether 316L is acceptable for the concentrated-salt piping. | [47 empty] | 制备连续配液系统改造-3000LHC釜法兰改TC口、2台HC浓盐罐法兰改TC口、BPE管道（316L+HC）；-问题：现场储罐为自行改造的TC口，需要征求客户意见； Retrofit of the continuous solution preparation system – convert the flanges of the 3000 L Hastelloy reactor to TC, convert the flanges of the 2 Hastelloy concentrated-salt vessels to TC, BPE piping (316L + Hastelloy). Open point: the TC connections on the existing site tanks were made in-house, so the customer's opinion is needed.
1 | 1213-R05 | 哈氏合金反应釜 / Hastelloy reactor | 3000L哈氏合金釜 / 3000 L Hastelloy reactor | C276 | 浓盐溶液 / Concentrated salt solution | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment | 该反应釜的釜口均为法兰结构，需要更换为快开的连接，整体满足4类管道设备需求。 All nozzles of this reactor are flanged and have to be changed to quick-connect fittings so that the whole unit meets the Category 4 piping and equipment requirements. 含反应釜加水的管路、放料到AT01、AT02的管路，需要满足4类管路需求，材质C276。 This includes the water charging line of the reactor and the discharge lines to AT01 and AT02, which have to meet the Category 4 piping requirements in C276. 生产这边无返厂维修窗口期，区域在生产礼来的三个片段肽。需要考虑现场改造方案。 Production has no window for a return-to-factory repair, because the area is producing the three fragment peptides for Eli Lilly. An on-site modification concept is therefore needed. | 方案一：利旧多肽3预计10月底到货 Option 1: reuse the unit from Peptide Building 3, expected to arrive end of October 方案二：返厂改造60天（厂家未反馈准确时间，参考多肽3），多次与供货商沟通无法现场改造； Option 2: return-to-factory modification, 60 days (the vendor has not confirmed an exact time; based on Peptide Building 3). Repeated discussions with the vendor confirmed that on-site modification is not possible. 方案三：新采购100天； Option 3: buy new, 100 days | 釜体、搅拌、人孔、下口改造方案已经确定，厂家预计在10月中旬过来改造；图纸对接中； The modification concept for the vessel body, agitator, manway and bottom outlet is fixed; the vendor is expected on site in mid-October; drawings are being aligned. 哈氏合金阀门进行确认型号开始采购；预计50天才能到货； Hastelloy valve models are being confirmed and procurement is starting; delivery is expected to take 50 days. 使用多肽3的反应釜同步配套一套哈氏合金球阀； A set of Hastelloy ball valves will be supplied together with the reactor from Peptide Building 3. 反应釜没有pH插口，确认是否需要增加，今天确认； The reactor has no pH port; whether one has to be added is being confirmed today. | 设备材料到货后施工20天 / 20 days of installation work after the equipment and materials arrive | 方案一：15d Option 1: 15 d 方案二：7d Option 2: 7 d 方案三：15d Option 3: 15 d | 方案一：39d Option 1: 39 d 方案二：31d Option 2: 31 d 方案三：39d Option 3: 39 d | 序号 / No. | 工序 / Activity | 设备/材料 / Equipment / material | 货期/工期 / Lead time / duration | 预计到货时间 / Expected delivery date | 10月 / October | [16 empty] | 11月 / November | [25 empty] | 序号 / No. | 工序 / Activity | 设备/材料 / Equipment / material | 货期/工期 / Lead time / duration | 预计到货时间 / Expected delivery date | 10月 / October | [16 empty] | 11月 / November | [21 empty] | 12月 / December | [18 empty] | 2027-01-01
2 | 1211-HPPC03-AT01 | 配液搅拌罐（不带夹套） / Solution preparation agitated vessel (non-jacketed) | 有效容积500L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 500 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | C276 | 浓盐溶液 / Concentrated salt solution | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment | 该储罐下口出料阀门及上口部分管路存在，需要更换为快开或者NA后者喇叭口的形式；材质哈氏合金的；按照4类设备进行； The bottom discharge valve and part of the top piping of this tank remain; they have to be changed to quick-connect, NA or flare connections in Hastelloy, executed to the Category 4 equipment requirements. 含储罐到静态混合器到A/B相的管路按照四类管路进行。 This includes the piping from the tank via the static mixer to phases A and B, executed to the Category 4 piping requirements. | 方案一：使用英德316L储罐改造40天（前提是可以使用316L材质，生产评估中）； Option 1: modify a Yingde 316L storage tank, 40 days (provided that 316L is acceptable; under assessment by Production) 方案二：返厂改造60天（厂家未反馈准确时间，参考多肽3）； Option 2: return-to-factory modification, 60 days (the vendor has not confirmed an exact time; based on Peptide Building 3) 方案三：新采购100天； Option 3: buy new, 100 days | 方案1：赢得的储罐制作中，30+20天的交货周期推进中；图纸已经反馈厂家 Option 1: the Yingde tank is in production; the 30 + 20 day delivery schedule is being pushed; drawings have been returned to the vendor 方案2：图纸正在确认，环形大法兰需要返厂处理，货期暂未反馈。 Option 2: drawings are being confirmed; the large ring flange has to be reworked at the factory and no lead time has been given yet |  | 方案一：4d Option 1: 4 d 方案二：4d Option 2: 4 d 方案三：6d Option 3: 6 d | 方案一：28d Option 1: 28 d 方案二：28d Option 2: 28 d 方案三：30d Option 3: 30 d | [5 empty] | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 备注 / Remarks | [5 empty] | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 5 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 5 | 10 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 1 | 2 | 3 | 4 | 5 | 备注 / Remarks
3 | 1211-HPPC03-AT02 | 配液搅拌罐（不带夹套） / Solution preparation agitated vessel (non-jacketed) | 有效容积300L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 300 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | C276 | 浓盐溶液 / Concentrated salt solution | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment | 该储罐下口出料阀门及上口部分管路存在，需要更换为快开或者NA后者喇叭口的形式；材质哈氏合金的；按照4类设备进行； The bottom discharge valve and part of the top piping of this tank remain; they have to be changed to quick-connect, NA or flare connections in Hastelloy, executed to the Category 4 equipment requirements. 含储罐到静态混合器到A/B相的管路按照四类管路进行。 This includes the piping from the tank via the static mixer to phases A and B, executed to the Category 4 piping requirements. |  | 上口、下口法兰，厂家到场改造。图纸今天可以确认完毕。 Top and bottom flanges; the vendor will modify them on site. The drawings can be finalised today. |  |  |  | 1 | 设备采购 / Equipment procurement | 3000L HC釜配件到货 / Delivery of the 3000 L Hastelloy reactor parts | 40 | 10月20 / 20 Oct | [42 empty] | 已订购 / Ordered | 1 | 设备采购 / Equipment procurement | 3000L HC釜配件到货 / Delivery of the 3000 L Hastelloy reactor parts | 40 | 10月20 / 20 Oct | [63 empty] | 已订购 / Ordered | bar: 10月 / October 15 to 10月 / October 20
5 | 1211-HPPC03-T01 | 纯水储罐（不带夹套） / Purified water storage tank (non-jacketed) | 有效容积1000L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 1000 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 纯化水 / Purified water | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment | 已满足 / Already compliant | —— | 已满足 / Already compliant |  | - |  | 2 |  | YD储罐到货（316） / Delivery of the YD storage tanks (316L) | 40 | 10月20 / 20 Oct | [42 empty] | 已订购 / Ordered | 2 |  | 浓盐罐法兰改TC（HC） / Convert the concentrated-salt vessel flanges to TC (Hastelloy) | 40 | 10月20 / 20 Oct | [63 empty] | 已订购 / Ordered | bar: 10月 / October 15 to 10月 / October 20
6 | 1211-HPPC03-T02 | 乙腈储罐（不带夹套） / Acetonitrile storage tank (non-jacketed) | 有效容积1000L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 1000 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 新鲜乙腈、备用 / Fresh acetonitrile, spare | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment | 已满足 / Already compliant | —— | 已满足 / Already compliant |  | - |  | 3 |  | 离心泵到货（316） / Delivery of the centrifugal pumps (316L) | 42 | 10月25 / 25 Oct | [42 empty] | 未订购，预估到货时间 / Not ordered yet, estimated delivery date | 3 |  | 离心泵到货（316） / Delivery of the centrifugal pumps (316L) | 42 | 10月25 / 25 Oct | [63 empty] | 未订购，预估到货时间 / Not ordered yet, estimated delivery date | bar: 10月 / October 15 to 10月 / October 25
7 | 1211-HPPC03-T03 | 流动相A储罐（不带夹套） / Mobile phase A storage tank (non-jacketed) | 有效容积1000L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 1000 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 流动相A / Mobile phase A | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment | 已满足 / Already compliant | —— | 已满足 / Already compliant |  | - |  | 4 |  | 四元隔膜泵到货（316） / Delivery of the four-head diaphragm pumps (316L) | 25 | 10月10 / 10 Oct | [42 empty] | 已订购 / Ordered | 4 |  | 四元隔膜泵到货（316） / Delivery of the four-head diaphragm pumps (316L) | 25 | 10月10 / 10 Oct | [63 empty] | 已订购 / Ordered | bar: 10月 / October 15
8 | 1211-HPPC03-T04 | 流动相B储罐（不带夹套） / Mobile phase B storage tank (non-jacketed) | 有效容积1000L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 1000 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 流动相B / Mobile phase B | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment | 已满足 / Already compliant | —— | 已满足 / Already compliant |  | - |  | 5 |  | 自控阀门/仪表采购（316） / Procurement of control valves / instruments (316L) | 42 | 10月25 / 25 Oct | [42 empty] | 部分已订购、部分未订购，预估到货时间 Partly ordered, partly not ordered; estimated delivery date | 5 |  | 四元隔膜泵到货（HC） / Delivery of the four-head diaphragm pumps (Hastelloy) | 90 | 12月15 / 15 Dec | [63 empty] | 未订购，预估到货时间 / Not ordered yet, estimated delivery date | bar: 10月 / October 15 to 12月 / December 15
9 | 1211-HPPC03-T05 | 乙腈储罐（不带夹套） / Acetonitrile storage tank (non-jacketed) | 有效容积1000L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 1000 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 乙腈 / Acetonitrile | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment | 已满足 / Already compliant | —— | 已满足 / Already compliant |  | - |  | 6 |  | BPE管件采购（316） / Procurement of BPE fittings (316L) | 30 | 10月15 / 15 Oct | [42 empty] | 已订购 / Ordered | 6 |  | 自控阀门/仪表采购（316） / Procurement of control valves / instruments (316L) | 42 | 10月25 / 25 Oct | [63 empty] | 部分已订购、部分未订购，预估到货时间 Partly ordered, partly not ordered; estimated delivery date | bar: 10月 / October 15 to 10月 / October 25
10 | 1211-HPPC03-T03-P01 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：2.5m3/h 扬程：25m 卡箍连接 Rated flow 2.5 m³/h, head 25 m, clamp connection | SS316L | 流动相A / Mobile phase A | 台 / unit | 1 | 厂家配套 / Supplied by the equipment vendor | 采购离心泵替换，在询价 / Purchase replacement centrifugal pumps; quotations in progress | 预计35天 / Estimated 35 days | 等图纸签字后反馈厂家，采购流程今天审批完毕。合同尽快确认。 To be sent to the vendor once the drawings are signed; the procurement approval was completed today. The contract is to be confirmed as soon as possible. |  | 8d（打料精度、均一性、RSD均需要重新验证） 8 d (dosing accuracy, uniformity and RSD all have to be re-qualified) |  | 7 |  | BPE手动阀门（316） / BPE manual valves (316L) | 30 | 10月15 / 15 Oct | [42 empty] | 已订购 / Ordered | 7 |  | BPE管件采购（316） / Procurement of BPE fittings (316L) | 30 | 10月15 / 15 Oct | [63 empty] | 已订购 / Ordered | bar: 10月 / October 15
11 | 1211-HPPC03-T03-P02 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：3.2m3/h 扬程：25m 卡箍连接 定频 Rated flow 3.2 m³/h, head 25 m, clamp connection, fixed speed | SS316L | 流动相A定量输送 / Metered transfer of mobile phase A | 台 / unit | 1 | 需新采购 / New purchase required | [6 empty] | 8 | 现场改造 / On-site modification | 3000LHC釜现场管口改造 / On-site nozzle modification of the 3000 L Hastelloy reactor | 10 |  | 切口 / Nozzle cutting | [41 empty] | 提前切割罐口 / Cut the vessel nozzles in advance | 8 |  | BPE管件采购（HC） / Procurement of BPE fittings (Hastelloy) | 60 | 10月15 / 15 Oct | [63 empty] | 已订购 / Ordered | bar: 10月 / October 15 to 11月 / November 10
12 | 1211-HPPC03-T04-P01 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：2.5m3/h 扬程：25m 卡箍连接 Rated flow 2.5 m³/h, head 25 m, clamp connection | SS316L | 流动相B/新鲜乙腈 / Mobile phase B / fresh acetonitrile | 台 / unit | 1 | 厂家配套 / Supplied by the equipment vendor | [6 empty] | 9 |  | 3000LHC釜配管（316） Piping of the 3000 L Hastelloy reactor (316L) | 4 | [43 empty] | 除插底管外，其他为316L / Everything except the dip tube is 316L | 9 | 现场改造 / On-site modification | 3000LHC釜现场改TC口 / On-site conversion of the 3000 L Hastelloy reactor to TC connections | 13 |  | 10月 / October 15: 提前切口 / Cut the nozzles in advance; 10月 / October 21: 焊接、抛光 / Welding and polishing | 提前切割罐口 / Cut the vessel nozzles in advance
13 | 1211-HPPC03-WT01-P01 | 离心泵 / Centrifugal pump | 额定流量：3.2m3/h 扬程：20m 卡箍连接 Rated flow 3.2 m³/h, head 20 m, clamp connection | 304 | 制备废液 / Preparation waste liquid | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment | [6 empty] | 10 |  | 浓盐罐拆/装 / Removal / installation of the concentrated-salt vessels | 2 | [43 empty] | 需要等储罐到货 / Waiting for delivery of the storage tanks | 10 |  | 3000LHC釜配管（HC） / Piping of the 3000 L Hastelloy reactor (Hastelloy) | 4 | [64 empty] | 需要等HC件到货 / Waiting for delivery of the Hastelloy parts | bar: 11月 / November 11 to 11月 / November 14
14 | 1211-HPPC03-WT02-P01 | 离心泵 / Centrifugal pump | 额定流量：3.2m3/h 扬程：20m 卡箍连接 Rated flow 3.2 m³/h, head 20 m, clamp connection | 304 | 制备废液 / Preparation waste liquid | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment | [6 empty] | 11 |  | 泵及BPE管道更换 / Replacement of pumps and BPE piping | 19 | [43 empty] | —— | 11 |  | 浓盐罐现场法兰改TC口 / On-site conversion of the concentrated-salt vessel flanges to TC | 13 |  | 10月 / October 15: 提前切口 / Cut the nozzles in advance; 10月 / October 21: 焊接、抛光 / Welding and polishing | 只改法兰口，快开口维持现状 / Only the flanged nozzles are modified; the existing quick-connect nozzles stay as they are
15 | 1211-HPPC03-AT01-P01 | 卫生级四元隔膜泵 / Sanitary four-head diaphragm pump | 额定流量：3.0Lmin BPE接口 卡箍连接 Rated flow 3.0 L/min, BPE connection, clamp connection | 316L或C276 / 316L or C276 | 浓盐溶液 / Concentrated salt solution | 台 / unit | 1 | 需新采购 / New purchase required | 采购四元隔膜泵替换 / Purchase replacement four-head diaphragm pumps | 预计20天 / Estimated 20 days | 316L已经订货完毕，预计9月底到货，生产郭泽鹏走的流程。 The 316L units are ordered and are expected end of September; the request was raised by Production (Guo Zepeng). 哈氏合金的货期3个月，预计在12月份才能到货，已经下单。 The Hastelloy units have a 3-month lead time and are expected in December; the order is placed. |  | 8d（打料精度、均一性、RSD均需要重新验证） 8 d (dosing accuracy, uniformity and RSD all have to be re-qualified) |  | 12 |  | 电气、仪表安装 / Electrical and instrumentation installation | 10 | [43 empty] | —— | 12 |  | 浓盐罐改泵及HC管道 / Change the pumps and the Hastelloy piping of the concentrated-salt vessels | 4 | [64 empty] | HC泵到货后替换 / Replace once the Hastelloy pumps arrive | bar: 12月 / December 16
16 | 1211-HPPC03-AT02-P01 | 卫生级四元隔膜泵 / Sanitary four-head diaphragm pump | 额定流量：2.0Lmin BPE接口 卡箍连接 Rated flow 2.0 L/min, BPE connection, clamp connection | 316L或C276 / 316L or C276 | 浓盐溶液 / Concentrated salt solution | 台 / unit | 1 | 需新采购 / New purchase required | [6 empty] | 13 | 验证 / Qualification | 调试 / Commissioning | [44 empty] | 验证IQ与安装同步执行，打点结束后关闭IQ，IQ在程序调试阶段完成 IQ runs in parallel with installation; IQ is closed after the loop check and is completed during software commissioning | 13 |  | 其他储罐改泵及BPE管道 / Change the pumps and the BPE piping of the other storage tanks | 20 | bar: 10月 / October 15 to 11月 / November 5
17 | 1211-HPPC03-T01-P01 | 卫生级四元隔膜泵 / Sanitary four-head diaphragm pump | 额定流量：35Lmin BPE接口 卡箍连接 Rated flow 35 L/min, BPE connection, clamp connection | SS316L | 纯化水 / Purified water | 台 / unit | 1 | 需新采购 / New purchase required | [6 empty] | 14 |  | 打点 / Loop check | [44 empty] | —— | 14 |  | 电气、仪表安装 / Electrical and instrumentation installation | 10 | [64 empty] | —— | bar: 10月 / October 23 to 11月 / November 5
18 | 1211-HPPC03-T01-P02 | 卫生级四元隔膜泵 / Sanitary four-head diaphragm pump | 额定流量：3.0Lmin BPE接口 卡箍连接 Rated flow 3.0 L/min, BPE connection, clamp connection | SS316L | 纯化水 / Purified water | 台 / unit | 1 | 需新采购 / New purchase required | [6 empty] | 15 |  | OQ | [44 empty] | —— | 18 | 验证 / Qualification | 调试 / Commissioning | bar: 11月 / November 15 to 11月 / November 19
19 | 1211-HPPC03-T02-P01 | 卫生级四元隔膜泵 / Sanitary four-head diaphragm pump | 额定流量：5.0Lmin BPE接口 卡箍连接 Rated flow 5.0 L/min, BPE connection, clamp connection | SS316L | 新鲜乙腈 / Fresh acetonitrile | 台 / unit | 1 | 需新采购 / New purchase required | [6 empty] | 16 |  | PQ | [44 empty] | —— | 19 |  | 打点 / Loop check | bar: 11月 / November 10 to 11月 / November 11
20 | 1211-HPPC03-T02-P02 | 卫生级四元隔膜泵 / Sanitary four-head diaphragm pump | 额定流量：35Lmin BPE接口 卡箍连接 Rated flow 35 L/min, BPE connection, clamp connection | SS316L | 新鲜乙腈 / Fresh acetonitrile | 台 / unit | 1 | 需新采购 / New purchase required |  |  |  |  | 和设备一块验证即可 / Can be qualified together with the equipment |  | 17 | 设备准备 / Equipment preparation | 清洗 / Cleaning | [44 empty] | —— | 20 |  | OQ | bar: 11月 / November 20 to 11月 / November 23
| TJ4S-1213-R05-P01 | 卫生级四元隔膜泵 / Sanitary four-head diaphragm pump | 额定流量：35Lmin BPE接口 卡箍连接 Rated flow 35 L/min, BPE connection, clamp connection | 316L或C276 / 316L or C276 | 浓盐溶液 / Concentrated salt solution | 台 / unit | 1 | 需新采购 / New purchase required | [54 empty] | 21 |  | PQ | bar: 11月 / November 24 to 11月 / November 25
21 | 配件 / Components | 质量流量计（快开、BPE） / Mass flow meter (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— | 可满足 / Acceptable | [51 empty] | 22 | 设备准备 / Equipment preparation | 清洗 / Cleaning | bar: 11月 / November 26 to 11月 / November 27
22 |  | 气动隔膜调节阀（快开、BPE） Pneumatic diaphragm control valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 采购快开隔膜调节阀 / Purchase quick-connect diaphragm control valves | 42天 / 42 days | 都已经买出去了，预计到货时间， All have been issued for purchase; delivery dates are estimates, |  |  |  | 制备组分接收改造-更换泵（316L）、BPE管道（316L）；问题：现场储罐为自行改造的TC口，需要征求客户意见； Retrofit of the fraction receiving area – replace the pumps (316L) and the BPE piping (316L). Open point: the TC connections on the existing site tanks were made in-house, so the customer's opinion is needed. | [47 empty] | 23 | 增补验证 / Supplementary qualification | 增补IQ（材质、铭牌、PID） Supplementary IQ (materials, nameplates, P&ID) |  |  | 12月 / December 17: 不占时间 / No additional time needed
23 |  | 气动隔膜开关阀（快开、BPE） Pneumatic diaphragm on/off valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 采购快开隔膜调节阀 / Purchase quick-connect diaphragm control valves | 42天 / 42 days | 都已经买出去了， / All have been issued for purchase, |  |  |  | 序号 / No. | 工序 / Activity | 设备/材料 / Equipment / material | 货期/工期 / Lead time / duration | 预计到货时间 / Expected delivery date | 10月 / October | [11 empty] | 11月 / November | [30 empty] | 24 |  | 调试(泵、程序调试) / Commissioning (pumps, software) | bar: 12月 / December 17 to 12月 / December 18
24 |  | 气动调节阀（快开、BPE） / Pneumatic control valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 采购快开隔膜调节阀 / Purchase quick-connect diaphragm control valves | 35天 / 35 days | 都已经买出去了， / All have been issued for purchase, | [8 empty] | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 备注 / Remarks | 25 |  | OQ（保压试密、泵流速精度） / OQ (pressure-hold leak test, pump flow accuracy)
25 |  | 气动开关阀（快开、BPE） / Pneumatic on/off valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 采购快开隔膜调节阀 / Purchase quick-connect diaphragm control valves | 35天 / 35 days | 都已经买出去了， / All have been issued for purchase, |  |  |  | 1 | 设备采购 / Equipment procurement | 离心泵到货（316） / Delivery of the centrifugal pumps (316L) | 42 | 10月25 / 25 Oct | [42 empty] | 未订购，预估到货时间 / Not ordered yet, estimated delivery date | 26 |  | PQ（配液确认） / PQ (solution preparation confirmation) | bar: 10月 / October 20 to 10月 / October 25
26 |  | 雷达液位计 / Radar level transmitter | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— | 可满足 / Acceptable |  |  |  | 2 |  | 自控阀门/仪表采购（316） / Procurement of control valves / instruments (316L) | 42 | 10月25 / 25 Oct | [42 empty] | 部分已订购、部分未订购，预估到货时间 Partly ordered, partly not ordered; estimated delivery date | 27 | 设备准备 / Equipment preparation | 清洗 / Cleaning | bar: 10月 / October 20 to 10月 / October 25
27 |  | 音叉 / Tuning-fork level switch | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— | 可满足 / Acceptable |  |  |  | 3 |  | BPE管件采购（316） / Procurement of BPE fittings (316L) | 30 | 10月15 / 15 Oct | [42 empty] | 已订购 / Ordered | bar: 10月 / October 20
28 |  | 温度 / Temperature instrument | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— | 可满足 / Acceptable |  |  |  | 4 |  | BPE手动阀门（316） / BPE manual valves (316L) | 30 | 10月15 / 15 Oct | [42 empty] | 已订购 / Ordered | bar: 10月 / October 20
29 |  | PH / pH instrument | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— | 可满足 / Acceptable |  |  |  | 5 | 现场改造 / On-site modification | 现有泵及管道拆除 / Removal of the existing pumps and piping | 1 | [43 empty] | —— | bar: 10月 / October 20
30 |  | 压力 / Pressure instrument | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— | 可满足 / Acceptable |  |  |  | 6 |  | 新泵及BPE管道更换 / Replacement with new pumps and BPE piping | 15 | [43 empty] | —— | bar: 10月 / October 21 to 11月 / November 4
31 |  | 手动隔膜阀 / Manual diaphragm valve | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— | 可满足 / Acceptable |  |  |  | 7 |  | 电气、仪表安装 / Electrical and instrumentation installation | 7 | [43 empty] | —— | bar: 10月 / October 29 to 11月 / November 4
32 |  | BPE管道、管件 / BPE piping and fittings | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 整体按照BPE的管路替换，满足2D，排尽等4类管路需求 The piping is replaced entirely to BPE standard, meeting the 2D and drainability requirements for Category 4 piping | BPE管件28天；BPE阀门42天，哈氏合金件60天(确认能否316L替代） BPE fittings 28 days; BPE valves 42 days; Hastelloy parts 60 days (to be confirmed whether 316L can be used instead) | 都已经买出去了， / All have been issued for purchase, |  |  |  | 8 | 验证 / Qualification | 空调 / HVAC |  |  | 11月 / November 5: 涉及动火需要做一静一动5天培养 Hot work is involved, so one at-rest and one in-operation monitoring run with 5-day incubation is required | 验证IQ与安装同步执行 / IQ runs in parallel with installation
制备系统-D级区-设备清单-客户需求 Preparation system – Grade D area – equipment list – customer requirements | [14 empty] | 9 |  | 储罐、管路 / Storage tanks and piping | [44 empty] | —— | bar: 11月 / November 6 to 11月 / November 10
序号 / No. | 设备位号 / Equipment tag | 设备名称 / Equipment name | 技术参数 / Technical parameters | 设备材质 / Equipment material | 使用介质 / Process medium | 单位 / Unit | 数量 / Quantity | 方案 / Option | 改造需求 / Modification requirement | 采购周期 / Procurement lead time |  | 安装周期 / Installation duration | 验证周期 / Qualification duration | 总计时间 / Total time | 10 | 设备准别 / Equipment preparation | 清洗 / Cleaning | bar: 11月 / November 11 to 11月 / November 12
1 | 1211-HPPC03-AT03 | 组分接收搅拌罐（带夹套） / Fraction receiving agitated vessel (jacketed) | 1、有效容积8000L； 1. Working volume 8000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：316L不锈钢； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— | 可满足 / Acceptable | 设备材料到货后施工15天 / 15 days of installation work after the equipment and materials arrive | 3d | 21d
2 | 1211-HPPC03-AT04/AT05 | 组分接收搅拌罐（带夹套） / Fraction receiving agitated vessel (jacketed) | 1、有效容积3000L； 1. Working volume 3000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：316L不锈钢； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂等 / Various organic solvents | 台 / unit | 2 | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— | 可满足 / Acceptable
3 | 1211-HPPC03-AT06 | 样品搅拌罐（带夹套） / Sample agitated vessel (jacketed) | 1、有效容积1000L； 1. Working volume 1000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：316L不锈钢； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— | 可满足 / Acceptable |  |  |  | 超滤区改造-更换BPE管道（316L）-问题：现场储罐为自行改造的TC口，需要征求客户意见； Retrofit of the ultrafiltration area – replace the BPE piping (316L). Open point: the TC connections on the existing site tanks were made in-house, so the customer's opinion is needed.
4 | 1211-HPPC03-T06 | 顶样搅拌罐（带夹套） / Top-fraction sample agitated vessel (jacketed) | 1、有效容积1000L； 1. Working volume 1000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：316L不锈钢； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— | 可满足 / Acceptable |  |  |  | 序号 / No. | 工序 / Activity | 设备/材料 / Equipment / material | 货期/工期 / Lead time / duration | 预计到货时间 / Expected delivery date | 10月 / October 20: 10月 / October; 11月 / November 1: 11月 / November
5 | *** | 组分接收储罐（不带夹套） / Fraction receiving storage tank (non-jacketed) | 有效容积100L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 100 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 12 | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— | 可满足 / Acceptable | [8 empty] | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 备注 / Remarks
| 1211-HPPC03-AT03-P01 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：12.5m3/h 扬程：25m 卡箍连接 变频 Rated flow 12.5 m³/h, head 25 m, clamp connection, variable speed | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 需新采购 / New purchase required |  |  | 等图纸签字后反馈厂家，采购流程今天审批完毕。合同尽快确认。 To be sent to the vendor once the drawings are signed; the procurement approval was completed today. The contract is to be confirmed as soon as possible. |  |  |  | 1 | 设备采购 / Equipment procurement | 自控阀门/仪表采购（316） / Procurement of control valves / instruments (316L) | 42 | 10月25 / 25 Oct | [42 empty] | 部分已订购、部分未订购，预估到货时间 Partly ordered, partly not ordered; estimated delivery date | bar: 10月 / October 20 to 10月 / October 25
| 1211-HPPC03-AT03-P02 | 卫生级离心泵，到超滤 / Sanitary centrifugal pump, to ultrafiltration | 额定流量：2m3/h 扬程：20m 卡箍连接 定频 Rated flow 2 m³/h, head 20 m, clamp connection, fixed speed | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 需新采购 / New purchase required | [6 empty] | 2 |  | BPE管件采购（316） / Procurement of BPE fittings (316L) | 30 | 10月15 / 15 Oct | [42 empty] | 已订购 / Ordered | bar: 10月 / October 20
| 1211-HPPC03-AT04-P01 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：12.5m3/h 扬程：25m 卡箍连接 变频 Rated flow 12.5 m³/h, head 25 m, clamp connection, variable speed | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 需新采购 / New purchase required | [6 empty] | 3 |  | BPE手动阀门（316） / BPE manual valves (316L) | 30 | 10月15 / 15 Oct | [42 empty] | 已订购 / Ordered | bar: 10月 / October 20
| 1211-HPPC03-AT05-P01 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：12.5m3/h 扬程：25m 卡箍连接 变频 Rated flow 12.5 m³/h, head 25 m, clamp connection, variable speed | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 需新采购 / New purchase required | [6 empty] | 4 | 现场改造 / On-site modification | BPE管道更换 / Replacement of BPE piping | 5 | [43 empty] | —— | bar: 10月 / October 23 to 10月 / October 27
| 1211-HPPC03-AT06-P01 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：12.5m3/h 扬程：25m 卡箍连接 变频 Rated flow 12.5 m³/h, head 25 m, clamp connection, variable speed | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 需新采购 / New purchase required | [6 empty] | 5 |  | 电气、仪表安装 / Electrical and instrumentation installation | 3 | [43 empty] | —— | bar: 10月 / October 25 to 10月 / October 27
| 1211-HPPC03-T06-P01 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：3.2m3/h 扬程：25m 卡箍连接 定频 Rated flow 3.2 m³/h, head 25 m, clamp connection, fixed speed | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 需新采购 / New purchase required | [6 empty] | 6 | 验证 / Qualification | 空调 / HVAC |  |  | 10月 / October 28: 涉及动火需要做一静一动5天培养 Hot work is involved, so one at-rest and one in-operation monitoring run with 5-day incubation is required | 验证IQ与安装同步执行 / IQ runs in parallel with installation
6 | *** | 气动隔膜泵 / Pneumatic diaphragm pump | 5m³/h，25m，快开连接 / 5 m³/h, 25 m, quick-connect | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 2 | 现有已安装设备 / Existing installed equipment | 匀浆罐进料及出料 / Charging and discharging of the homogenisation vessel | 35天 / 35 days | 已完成 / Completed |  |  |  | 7 |  | 储罐、管路 / Storage tanks and piping | [44 empty] | —— | bar: 10月 / October 29 to 11月 / November 2
| *** | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：2m3/h 扬程：20m 卡箍连接 定频 Rated flow 2 m³/h, head 20 m, clamp connection, fixed speed | SS316L | 合格组分 / In-spec fractions | 台 / unit | 1 |  |  |  | 等图纸签字后反馈厂家，采购流程今天审批完毕。合同尽快确认。 To be sent to the vendor once the drawings are signed; the procurement approval was completed today. The contract is to be confirmed as soon as possible. |  |  |  | 8 | 设备准别 / Equipment preparation | 清洗 / Cleaning | bar: 11月 / November 3 to 11月 / November 4
| *** | 气动隔膜泵 / Pneumatic diaphragm pump | 额定流量：5m3/h 扬程：25m 卡箍连接 Rated flow 5 m³/h, head 25 m, clamp connection | SS316L | 不合格组分 / Out-of-spec fractions | 台 / unit | 1 |  |  |  | 满足使用 / Fit for use
7 | 配件 / Components | 质量流量计（快开、BPE） / Mass flow meter (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— | 可满足 / Acceptable
8 |  | 气动隔膜调节阀（快开、BPE） Pneumatic diaphragm control valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 采购快开调节阀 / Purchase quick-connect control valves | 42天 / 42 days | 都已经买出去了， / All have been issued for purchase,
9 |  | 气动隔膜开关阀（快开、BPE） Pneumatic diaphragm on/off valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 采购快开开关阀 / Purchase quick-connect on/off valves | 42天 / 42 days | 都已经买出去了， / All have been issued for purchase, |  |  |  | 沉淀区改造-更换80L储罐（316L）、BPE管道（316L）-问题：现场设备（釜、三合一、储罐）为自行改造的TC口，需要征求客户意见； Retrofit of the precipitation area – replace the 80 L storage tank (316L) and the BPE piping (316L). Open point: the TC connections on the existing site equipment (reactor, filter-dryer, storage tanks) were made in-house, so the customer's opinion is needed.
10 |  | 气动调节阀（快开、BPE） / Pneumatic control valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 采购快开调节阀 / Purchase quick-connect control valves | 35天 / 35 days | 都已经买出去了， / All have been issued for purchase, |  |  |  | 序号 / No. | 工序 / Activity | 设备/材料 / Equipment / material | 货期/工期 / Lead time / duration | 预计到货时间 / Expected delivery date | 10月 / October 20: 10月 / October; 11月 / November 1: 11月 / November
11 |  | 气动开关阀（快开、BPE） / Pneumatic on/off valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 采购快开开关阀 / Purchase quick-connect on/off valves | 35天 / 35 days | 都已经买出去了， / All have been issued for purchase, | [8 empty] | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 备注 / Remarks
12 |  | 雷达液位计 / Radar level transmitter | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— | 可满足 / Acceptable |  |  |  | 1 | 设备采购 / Equipment procurement | YD150L储罐到货（316） Delivery of the YD 150 L storage tank (316L) | 40 | 10月20 / 20 Oct | [42 empty] | 已订购 / Ordered | bar: 10月 / October 20
13 |  | 音叉 / Tuning-fork level switch | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— | 可满足 / Acceptable |  |  |  | 2 |  | 离心泵到货（316） / Delivery of the centrifugal pumps (316L) | 42 | 10月25 / 25 Oct | [42 empty] | 未订购，预估到货时间 / Not ordered yet, estimated delivery date | bar: 10月 / October 20 to 10月 / October 25
14 |  | 温度 / Temperature instrument | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— | 可满足 / Acceptable |  |  |  | 3 |  | 自控阀门/仪表采购（316） / Procurement of control valves / instruments (316L) | 42 | 10月25 / 25 Oct | [42 empty] | 部分已订购、部分未订购，预估到货时间 Partly ordered, partly not ordered; estimated delivery date | bar: 10月 / October 20 to 10月 / October 25
15 |  | PH / pH instrument | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— | 可满足 / Acceptable |  |  |  | 4 |  | BPE管件采购（316） / Procurement of BPE fittings (316L) | 30 | 10月15 / 15 Oct | [42 empty] | 已订购 / Ordered | bar: 10月 / October 20
16 |  | 压力 / Pressure instrument | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— | 可满足 / Acceptable |  |  |  | 5 |  | BPE手动阀门（316） / BPE manual valves (316L) | 30 | 10月15 / 15 Oct | [42 empty] | 已订购 / Ordered | bar: 10月 / October 20
17 |  | 手动隔膜阀 / Manual diaphragm valve | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— | 可满足 / Acceptable |  |  |  | 6 |  | 80L罐拆/装、湿氮气安装 / Removal / installation of the 80 L vessel, installation of the wet nitrogen supply | 1 | [43 empty] | 需要等储罐到货 / Waiting for delivery of the storage tanks | bar: 10月 / October 21
18 |  | BPE管道、管件 / BPE piping and fittings | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 整体按照BPE的管路替换，满足2D，排尽等4类管路需求 The piping is replaced entirely to BPE standard, meeting the 2D and drainability requirements for Category 4 piping | BPE管件28天；BPE阀门42天 BPE fittings 28 days; BPE valves 42 days | 都已经买出去了，今天T型阀进行下单补充采购。 All have been issued for purchase; a supplementary order for the T-valves is being placed today. |  |  |  | 7 |  | 泵及BPE管道更换 / Replacement of pumps and BPE piping | 15 | [43 empty] | —— | bar: 10月 / October 21 to 11月 / November 4
超滤系统设备清单-自己评估 / Ultrafiltration system equipment list – internal assessment | [14 empty] | 8 |  | 电气、仪表安装 / Electrical and instrumentation installation | 7 | [43 empty] | —— | bar: 10月 / October 29 to 11月 / November 4
序号 / No. | 设备位号 / Equipment tag | 设备名称 / Equipment name | 技术参数 / Technical parameters | 设备材质 / Equipment material | 使用介质 / Process medium | 单位 / Unit | 数量 / Quantity | 方案 / Option | 改造需求 / Modification requirement | 采购周期 / Procurement lead time |  | 安装周期 / Installation duration | 验证周期 / Qualification duration | 总计时间 / Total time | 9 | 验证 / Qualification | 空调 / HVAC |  |  | 11月 / November 5: 涉及动火需要做一静一动5天培养 Hot work is involved, so one at-rest and one in-operation monitoring run with 5-day incubation is required | 验证IQ与安装同步执行 / IQ runs in parallel with installation
1 | 1211-TFF01-T01 | 超滤接收储罐（带夹套） / Ultrafiltration receiving storage tank (jacketed) | 1、有效容积1000L； 1. Working volume 1000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— | 可满足 / Acceptable | 管件到货后施工预计5天 / Around 5 days of installation work after the fittings arrive | 3d | 11d | 10 |  | 储罐、管路 / Storage tanks and piping | [44 empty] | —— | bar: 11月 / November 6 to 11月 / November 10
2 | 配件 / Components | 质量流量计（快开、BPE） / Mass flow meter (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— | 可满足 / Acceptable |  |  |  | 11 | 设备准别 / Equipment preparation | 清洗 / Cleaning | bar: 11月 / November 11 to 11月 / November 12
3 |  | 气动隔膜调节阀（快开、BPE） Pneumatic diaphragm control valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— | 可满足 / Acceptable
4 |  | 气动隔膜开关阀（快开、BPE） Pneumatic diaphragm on/off valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— | 可满足 / Acceptable
5 |  | 手动隔膜阀 / Manual diaphragm valve | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— | 可满足 / Acceptable
6 |  | BPE管道、管件 / BPE piping and fittings | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 评估甲醇、乙腈水、氢氧化钠溶液是否需要更换为BPE管路。 Assess whether the methanol, acetonitrile / water and sodium hydroxide solution lines have to be changed to BPE piping. | BPE管件28天；BPE阀门42天 BPE fittings 28 days; BPE valves 42 days | 都已经买出去了，今天T型阀进行下单补充采购。 All have been issued for purchase; a supplementary order for the T-valves is being placed today.
| *** | 气动隔膜泵 / Pneumatic diaphragm pump | 额定流量：5m3/h 扬程：25m 卡箍连接 Rated flow 5 m³/h, head 25 m, clamp connection | SS316L |  | 台 / unit | 1 |  |  |  | 可满足 / Acceptable
| TJ4S-1211-TFF02-WTK01-MP01 | 离心泵 / Centrifugal pump | 额定流量：3.2m3/h 扬程：20m Rated flow 3.2 m³/h, head 20 m | 304 | 超滤废液 / Ultrafiltration waste liquid | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment |  |  | 可满足 / Acceptable
| TJ4S-1211-TFF02-WTK01-MP02 | 离心泵 / Centrifugal pump | 额定流量：3.2m3/h 扬程：20m Rated flow 3.2 m³/h, head 20 m | 304 | 超滤废液 / Ultrafiltration waste liquid | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment |  |  | 可满足 / Acceptable
沉淀釜区设备清单-自己评估 / Precipitation reactor area equipment list – internal assessment
序号 / No. | 设备位号 / Equipment tag | 设备名称 / Equipment name | 技术参数 / Technical parameters | 设备材质 / Equipment material | 使用介质 / Process medium | 单位 / Unit | 数量 / Quantity | 方案 / Option | 改造需求 / Modification requirement | 采购周期 / Procurement lead time | 09/17目前进展 / Status as of 09/17 | 安装周期 / Installation duration | 验证周期 / Qualification duration | 总计时间 / Total time
1 | 1211-R01 | 析晶釜 / Crystallizer | 1、有效容积2000L； 1. Working volume 2000 L; 2、釜内设计温度-25~200℃，夹套设计温度-25~220℃； 2. Reactor design temperature −25 to 200 °C, jacket design temperature −25 to 220 °C; 3、釜内设计压力-0.1~0.4MPa；夹套工作压力0.6Mpa； 3. Reactor design pressure −0.1 to 0.4 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：304不锈钢衬C22或C276； Product contact: 304 stainless steel lined with C22 or C276; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、酸、碱等 / Various organic solvents, acids, bases, etc. | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— | 可满足 / Acceptable | 设备材料到货后施工15天 / 15 days of installation work after the equipment and materials arrive
3 | 1211-AT01 | 搅拌罐 / Agitated vessel | 1、有效容积600L； 1. Working volume 600 L; 2、罐内设计温度-25~200℃，夹套设计温度-25~220℃； 2. Vessel design temperature −25 to 200 °C, jacket design temperature −25 to 220 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：316L不锈钢； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、盐溶液等 / Various organic solvents, salt solutions, etc. | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment | 管路需要满足BPE标准，按照4类管路进行改造。 The piping has to meet the BPE standard and is modified to the Category 4 piping requirements. 管线、排尽不满足2D Piping and drainability do not meet 2D | BPE管件28天；BPE阀门42天 BPE fittings 28 days; BPE valves 42 days | 都已经买出去了，今天T型阀进行下单补充采购。 All have been issued for purchase; a supplementary order for the T-valves is being placed today. |  | 方案一：3d Option 1: 3 d 方案二：7d Option 2: 7 d | 方案一：21dd Option 1: 21 d 方案二：25d Option 2: 25 d
4 | 1211-AT02 | 搅拌罐 / Agitated vessel | 1、有效容积80L； 1. Working volume 80 L; 2、罐内设计温度-25~200℃，夹套设计温度-25~220℃； 2. Vessel design temperature −25 to 200 °C, jacket design temperature −25 to 220 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：316L不锈钢； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、酸、碱等 / Various organic solvents, acids, bases, etc. | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment | 下口存在法兰，需要进行改造。滴加碱液的管路确认需要更换BPE管路。 There is a flange at the bottom outlet that has to be modified. It is confirmed that the caustic dosing line has to be changed to BPE piping. | 方案一：使用英德现货改造40天；（前提是制备配盐罐不换） Option 1: modify a Yingde stock tank, 40 days (provided the salt preparation vessel is not replaced) 方案二：现场为哈氏合金材质，改造材料需要60天；涉及压力容器改造； Option 2: the existing unit is Hastelloy, so the modification material takes 60 days; a pressure-vessel modification is involved | 方案一：150L罐进行改造；东富龙的储罐沟通后采购流程后放弃选择。 Option 1: modify the 150 L vessel; the Tofflon tank was dropped after the procurement discussions. 方案2：亚光安排施工人员过来改造。 Option 2: Yaguang will send fitters for the on-site modification.
| TJ4S-1211-AT02-P02 | 气动隔膜泵 / Pneumatic diaphragm pump | 额定流量：5m3/h 扬程：25m 卡箍连接 Rated flow 5 m³/h, head 25 m, clamp connection | SS316L |  | 台 / unit | 1 |  |  |  | 可满足 / Acceptable
15 | TJ4S-1211-AT01-P01 | 卫生级四元隔膜泵 / Sanitary four-head diaphragm pump | 额定流量：200L/h BPE接口 卡箍连接 Rated flow 200 L/h, BPE connection, clamp connection | 316L | 浓盐溶液 / Concentrated salt solution | 台 / unit | 1 | 需新采购 / New purchase required | 采购四元隔膜泵替换 / Purchase replacement four-head diaphragm pumps |  | 已采购，预计9月底到货 / Purchased, expected end of September
16 | TJ4S-1211-AT02-P01 | 卫生级四元隔膜泵 / Sanitary four-head diaphragm pump | 额定流量：20L/h BPE接口 卡箍连接 Rated flow 20 L/h, BPE connection, clamp connection | 316L | 浓盐溶液 / Concentrated salt solution | 台 / unit | 1 | 需新采购 / New purchase required |  |  | 已采购，预计9月底到货 / Purchased, expected end of September
5 | 1211-Fd01 | 三合一 / Filter-dryer | 1、设备尺寸DN1200； 1. Equipment size DN1200; 2、罐内设计温度-25~200℃，夹套设计温度-25~220℃； 2. Vessel design temperature −25 to 200 °C, jacket design temperature −25 to 220 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：304不锈钢衬C22或C276； Product contact: 304 stainless steel lined with C22 or C276; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、酸、碱等 / Various organic solvents, acids, bases, etc. | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— | 可满足 / Acceptable
7 | *** | 旋分筛 / Rotary sifter | 处理量200kg/h. Throughput 200 kg/h. | SS316L | 固体 / Solids | 台 / unit | 1 | 购新安装 / Purchase new and install | 市场上持续寻找中； / Still being sourced on the market; | —— | 生产市场上持续寻找中； / Production is still sourcing it on the market; |  | 15d | 33d
8 | 配件 / Components | 质量流量计（快开、BPE） / Mass flow meter (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 可满足 / Acceptable | —— | 可满足 / Acceptable |  | - | -
9 |  | 气动隔膜调节阀（快开、BPE） Pneumatic diaphragm control valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 可满足 / Acceptable | —— | 可满足 / Acceptable
10 |  | 气动隔膜开关阀（快开、BPE） Pneumatic diaphragm on/off valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 可满足 / Acceptable | —— | 可满足 / Acceptable
11 |  | 手动隔膜阀 / Manual diaphragm valve | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 可满足 / Acceptable | —— | 可满足 / Acceptable
12 |  | BPE管道、管件 / BPE piping and fittings | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 三合一淋洗管路不是满足BPE； The spray piping of the filter-dryer does not meet BPE; 600L罐管路不满足； the piping of the 600 L vessel does not comply; 管路需要满足BPE标准，按照4类管路进行改造。管线、排尽不满足2D the piping has to meet the BPE standard and is modified to the Category 4 piping requirements. Piping and drainability do not meet 2D | BPE管件28天；BPE阀门42天 BPE fittings 28 days; BPE valves 42 days | 都已经买出去了，今天T型阀进行下单补充采购。 All have been issued for purchase; a supplementary order for the T-valves is being placed today. |  | 3d | 21d
| TJ4S-1211-FD01-Tr01-P01 | 气动隔膜泵 / Pneumatic diaphragm pump | 额定流量：5m3/h 扬程：30m 卡箍连接 Rated flow 5 m³/h, head 30 m, clamp connection | 防腐 / Corrosion-resistant |  | 台 / unit | 1 |  |  |  | 可满足 / Acceptable
| TJ4S-1211-FD01-Tr01-P02 | 气动隔膜泵 / Pneumatic diaphragm pump | 额定流量：5m3/h 扬程：30m 卡箍连接 Rated flow 5 m³/h, head 30 m, clamp connection | 防腐 / Corrosion-resistant |  | 台 / unit | 1 |  |  |  | 可满足 / Acceptable
| TJ4S-1212-FD06-Tr01-P01 | 气动隔膜泵 / Pneumatic diaphragm pump | 额定流量：5m3/h 扬程：30m 卡箍连接 Rated flow 5 m³/h, head 30 m, clamp connection | 防腐 / Corrosion-resistant |  | 台 / unit | 1 |  |  |  | 可满足 / Acceptable
| *** | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：2m3/h 扬程：20m 卡箍连接 定频 Rated flow 2 m³/h, head 20 m, clamp connection, fixed speed | SS316L |  | 台 / unit | 2 |  | 注射水泵 / Water-for-injection pump |  | 已经采购。 / Already purchased.

## 方案2 Option 2 New Batch (hidden)
多肽厂房2新做批次配液系统-设备采购清单-按PID图安装 Peptide Building 2, new batch solution preparation system – equipment purchasing list – installed according to the P&ID
制备配液系统设备清单 / Preparation / solution system equipment list
序号 / No. | 设备位号 / Equipment tag | 设备名称 / Equipment name | 技术参数 / Technical parameters | 设备材质 / Equipment material | 使用介质 / Process medium | 单位 / Unit | 数量 / Quantity | 设备来源 / Equipment source | 09/17/2026进展 / Status as of 09/17/2026 | 采购周期 / Procurement lead time | 安装周期 / Installation duration | 验证周期 / Qualification duration | 加3天清洗总计时间 / Total time including 3 days of cleaning | 技术要求 / Technical requirements
1 | *** | 配盐搅拌罐（带夹套） / Salt solution agitated vessel (jacketed) | 1、有效容积3000L； 1. Working volume 3000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：304不锈钢衬C22或C276； Product contact: 304 stainless steel lined with C22 or C276; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、酸、碱等 / Various organic solvents, acids, bases, etc. | 台 / unit | 0 | 考虑多肽3厂房改造完毕符合BPE的3000L哈市合金釜 Assumes the BPE-compliant 3000 L Hastelloy reactor released by the Peptide Building 3 retrofit | 10月底到货，增加pH计口确认货期影响；厂家阀门同步配置上； Arrives end of October; the impact of adding a pH port on the lead time is being confirmed; the vendor is fitting the valves at the same time | 10月末到 / End of October | 30 | 1、工程打点3d，调试和验证共15d(程序调试4d+泵调试3d+验证8d：OQ4d、程序EOQ2d，PQ2d) 1. Engineering loop check 3 d; commissioning and qualification 15 d in total (software commissioning 4 d + pump commissioning 3 d + qualification 8 d: OQ 4 d, software EOQ 2 d, PQ 2 d) 2、影响制备区域的环境（涉及穿墙管焊接），需要重新做相应的微生物检测，和配液系统同步，不影响整体放行的时间 2. The environment of the preparation area is affected (wall penetration welding is involved), so the corresponding microbial monitoring has to be repeated in parallel with the solution system; this does not affect the overall release date 3、CNC区域的空调重新OQ，不影响整体的放行时间 3. The HVAC of the CNC area has to be re-qualified (OQ); this does not affect the overall release date | 51d | 1、设备应满足ASME BPE要求，包括不限于如下要求： 1. The equipment shall comply with ASME BPE, including but not limited to: （1）设备接口采用NA接口，满足2D要求；接口尺寸及数量以确认图纸为准； (1) NA-type connections meeting the 2D drainability requirement; connection sizes and quantities as per the approved drawings; （2）设计淋洗口，需配淋洗球，满足全面清洗且通过核黄素清洗验证； (2) Spray port with spray ball, giving full coverage and passing the riboflavin coverage test; （3）出料口焊接隔膜阀，满足2D要求； (3) Diaphragm valve welded to the outlet, meeting the 2D requirement; （4）外表面抛光粗糙度<0.8um，内壁抛光粗糙度<0.4um； (4) External surface roughness < 0.8 µm, internal surface roughness < 0.4 µm; (5) 设备的原材、配件、生产制造及验收应严格按照ASME BPE要求进行，并提供相关证明资料； (5) Raw materials, components, manufacturing and acceptance strictly in line with ASME BPE, with the supporting documentation provided; 2、电机、减速机要求： 2. Motor and gearbox: （1）采用国内知名品牌；整体外包不锈钢，满足卫生级要求； (1) Well-known domestic brand; fully stainless-steel clad to sanitary standard; （2）防爆等级 ExdIIBT4 Gb，防护等级不低于IP55;电机能效不低于二级； (2) Explosion protection Ex d IIB T4 Gb, ingress protection not lower than IP55; motor efficiency class 2 or better; 3、机封采用双端面卫生级干磨机封，采用国内知名品牌； 3. Double-end sanitary dry-running mechanical seal from a well-known domestic brand; 4、搅拌材质与罐体一直，搅拌形式最终确认图纸为准； 4. Agitator material identical to the vessel; agitator design as per the approved drawings; 5、保温厚度满足温度要求，外壳采用3mm不锈钢，外表抛光粗糙度<0.8um， 5. Insulation thickness to suit the temperature requirement; cladding in 3 mm stainless steel with an external surface roughness < 0.8 µm, | 制备批次配液系统-使用多肽3的3000LHC釜、YD储罐（316L）；问题：现场反应釜为自行改造的TC口，需要征求客户意见；浓盐管道需要评估316L能否满足？ Batch solution preparation system – use the 3000 L Hastelloy reactor from Peptide Building 3 and YD storage tanks (316L). Open points: the TC connections on the existing site reactor were made in-house, so the customer's opinion is needed; it must be assessed whether 316L is acceptable for the concentrated-salt piping. | [61 empty] | 制备批次配液系统-使用多肽3的3000LHC釜、YD储罐（316L）；问题：现场反应釜为自行改造的TC口，需要征求客户意见； Batch solution preparation system – use the 3000 L Hastelloy reactor from Peptide Building 3 and YD storage tanks (316L). Open point: the TC connections on the existing site reactor were made in-house, so the customer's opinion is needed.
2 | *** | 配盐搅拌罐（带夹套） / Salt solution agitated vessel (jacketed) | 1、有效容积3000L； 1. Working volume 3000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：SS316L； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、酸、碱等 / Various organic solvents, acids, bases, etc. | 台 / unit | 1 | 利旧5000L储罐（1）-改造6周（加搅拌、防爆电机、下口阀） Reuse 5000 L storage tank (1) – 6-week modification (add agitator, explosion-proof motor, bottom outlet valve) | 30+20供货周期，已经开始制作； 30 + 20 day lead time; manufacturing has started | 42 |  |  |  |  | 序号 / No. | 工序 / Activity | 设备/材料 / Equipment / material | 货期/工期 / Lead time / duration | 预计到货时间 / Expected delivery date | 10月 / October | [21 empty] | 11月 / November | [29 empty] | 12月 / December |  |  |  | 备注 / Remarks | 序号 / No. | 工序 / Activity | 设备/材料 / Equipment / material | 货期/工期 / Lead time / duration | 预计到货时间 / Expected delivery date | 10月 / October | [21 empty] | 11月 / November | [29 empty] | 12月 / December | [18 empty] | 2027-01-01 | [7 empty] | 备注 / Remarks
3 | *** | 流动相A搅拌罐（带夹套） / Mobile phase A agitated vessel (jacketed) | 1、有效容积3000L； 1. Working volume 3000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：SS316L； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、酸、碱等 / Various organic solvents, acids, bases, etc. | 台 / unit | 1 | 利旧5000L储罐（2）-改造6周（加搅拌、防爆电机、下口阀） Reuse 5000 L storage tank (2) – 6-week modification (add agitator, explosion-proof motor, bottom outlet valve) | 30+20供货周期，已经开始制作； 30 + 20 day lead time; manufacturing has started | 42 | [9 empty] | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 1 | 2 | 3 | 4 | [6 empty] | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 5 | 10 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
4 | *** | 流动相B搅拌罐（带夹套） / Mobile phase B agitated vessel (jacketed) | 1、有效容积3000L； 1. Working volume 3000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：SS316L； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、酸、碱等 / Various organic solvents, acids, bases, etc. | 台 / unit | 1 | 利旧5000L储罐（3）-改造6周（加搅拌、防爆电机、下口阀） Reuse 5000 L storage tank (3) – 6-week modification (add agitator, explosion-proof motor, bottom outlet valve) | 30+20供货周期，已经开始制作； 30 + 20 day lead time; manufacturing has started | 42 |  |  |  |  | 1 | 设备采购 / Equipment procurement | 3000L HC釜到货（多肽3） Delivery of the 3000 L Hastelloy reactor (from Peptide Building 3) | 50 | 10月31 / 31 Oct | [56 empty] | 已订购 / Ordered | 1 | 设备采购 / Equipment procurement | 3000L HC釜到货（多肽3） Delivery of the 3000 L Hastelloy reactor (from Peptide Building 3) | 50 | 10月31 / 31 Oct | [79 empty] | 已订购 / Ordered | bar: 10月 / October 10 to 10月 / October 31
5 | *** | 乙腈储罐（不带夹套） / Acetonitrile storage tank (non-jacketed) | 有效容积1000L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 1000 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 新鲜乙腈 / Fresh acetonitrile | 台 / unit | 1 | 利旧1500L储罐（4）-改造6周（加搅拌、防爆电机、下口阀） Reuse 1500 L storage tank (4) – 6-week modification (add agitator, explosion-proof motor, bottom outlet valve) | 30+20供货周期，已经开始制作； 30 + 20 day lead time; manufacturing has started | 42 |  |  |  | 设备应满足ASME BPE要求，包括不限于如下要求： The equipment shall comply with ASME BPE, including but not limited to: （1）设备接口采用NA接口，满足2D要求；接口尺寸及数量以确认图纸为准； (1) NA-type connections meeting the 2D drainability requirement; connection sizes and quantities as per the approved drawings; （2）设计淋洗口，需配淋洗球，满足全面清洗且通过核黄素清洗验证； (2) Spray port with spray ball, giving full coverage and passing the riboflavin coverage test; （3）出料口焊接隔膜阀，满足2D要求； (3) Diaphragm valve welded to the outlet, meeting the 2D requirement; （4）外表面抛光粗糙度<0.8um，内壁抛光粗糙度<0.4um； (4) External surface roughness < 0.8 µm, internal surface roughness < 0.4 µm; (5) 设备的原材、配件、生产制造及验收应严格按照ASME BPE要求进行，并提供相关证明资料； (5) Raw materials, components, manufacturing and acceptance strictly in line with ASME BPE, with the supporting documentation provided; | 2 |  | YD储罐到货（316） / Delivery of the YD storage tanks (316L) | 30 | 10月15 / 15 Oct | [56 empty] | 已订购 / Ordered | 2 |  | YD储罐到货（316） / Delivery of the YD storage tanks (316L) | 30 | 10月15 / 15 Oct | [79 empty] | 已订购 / Ordered | bar: 10月 / October 10 to 10月 / October 15
6 | *** | 甲醇储罐（不带夹套） / Methanol storage tank (non-jacketed) | 有效容积1000L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 1000 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 新鲜甲醇 / Fresh methanol | 台 / unit | 0 | —— | —— | 42 |  |  |  |  | 3 |  | 离心泵到货（316） / Delivery of the centrifugal pumps (316L) | 42 | 10月25 / 25 Oct | [56 empty] | 未订购，预估到货时间 / Not ordered yet, estimated delivery date | 3 |  | 离心泵到货（316） / Delivery of the centrifugal pumps (316L) | 42 | 10月25 / 25 Oct | [79 empty] | 未订购，预估到货时间 / Not ordered yet, estimated delivery date | bar: 10月 / October 10 to 10月 / October 25
7 | *** | 纯化水储罐（不带夹套） / Purified water storage tank (non-jacketed) | 有效容积1000L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 1000 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 纯换水 / Purified water | 台 / unit | 1 | 利旧1500L储罐（5）-改造6周（加搅拌、防爆电机、下口阀） Reuse 1500 L storage tank (5) – 6-week modification (add agitator, explosion-proof motor, bottom outlet valve) | 30+20供货周期，已经开始制作； 30 + 20 day lead time; manufacturing has started | 42 |  |  |  |  | 4 |  | 自控阀门/仪表采购（316） / Procurement of control valves / instruments (316L) | 42 | 10月25 / 25 Oct | [56 empty] | 部分已订购、部分未订购，预估到货时间 Partly ordered, partly not ordered; estimated delivery date | 4 |  | 离心泵到货（HC） / Delivery of the centrifugal pumps (Hastelloy) | 90 | 12月15 / 15 Dec | [79 empty] | 未订购，预估到货时间 / Not ordered yet, estimated delivery date | bar: 10月 / October 10 to 12月 / December 15
8 | 1211-HPPC03-AT07-P01 | 卫生级四元隔膜泵 / Sanitary four-head diaphragm pump | 额定流量：10.0Lmin BPE接口 卡箍连接 Rated flow 10.0 L/min, BPE connection, clamp connection | C276 | 浓盐溶液 / Concentrated salt solution | 台 / unit | 1 | 新采购 / Newly purchased | 316L已经订货完毕，预计9月底到货，生产郭泽鹏走的流程。 The 316L units are ordered and are expected end of September; the request was raised by Production (Guo Zepeng). 哈氏合金的货期3个月，预计在12月份才能到货，已经下单。 The Hastelloy units have a 3-month lead time and are expected in December; the order is placed. | 45 |  |  |  | 设备应满足ASME BPE要求，包括不限于如下要求： The equipment shall comply with ASME BPE, including but not limited to: （1）设备接口采用NA接口，满足2D要求，设备腔体可排净； (1) NA-type connections meeting the 2D drainability requirement, with a fully drainable equipment body; （2）外表面抛光粗糙度<0.8um，内壁抛光粗糙度<0.4um； (2) External surface roughness < 0.8 µm, internal surface roughness < 0.4 µm; （3）设备的原材、配件、生产制造及验收应严格按照ASME BPE要求进行，并提供相关证明资料； (3) Raw materials, components, manufacturing and acceptance strictly in line with ASME BPE, with the supporting documentation provided; | 5 |  | BPE管件采购（316） / Procurement of BPE fittings (316L) | 30 | 10月15 / 15 Oct | [56 empty] | 已订购 / Ordered | 5 |  | 自控阀门/仪表采购（316） / Procurement of control valves / instruments (316L) | 42 | 10月25 / 25 Oct | [79 empty] | 部分已订购、部分未订购，预估到货时间 Partly ordered, partly not ordered; estimated delivery date | bar: 10月 / October 10 to 10月 / October 25
9 | 1211-HPPC03-AT08-P01 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：12.5m3/h 扬程：25m 卡箍连接；变频 Rated flow 12.5 m³/h, head 25 m, clamp connection; variable speed | SS316L | 流动相A / Mobile phase A | 台 / unit | 1 | 新采购 / Newly purchased | 确认图纸中，合同今天，明天催促完毕，预计10月中下旬到货。 Drawings are being confirmed; the contract will be chased today and tomorrow; delivery is expected in the second half of October. | 35 |  |  |  |  | 6 |  | DCS系统供货 / Supply of the DCS system | 45 | 10月31 / 31 Oct | [56 empty] | 未订购，预估到货时间 / Not ordered yet, estimated delivery date | 6 |  | BPE管件采购（316） / Procurement of BPE fittings (316L) | 30 | 10月15 / 15 Oct | [79 empty] | 已订购 / Ordered | bar: 10月 / October 10 to 10月 / October 15
| 1211-HPPC03-AT08-P02 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：3.2m3/h 扬程：25m 卡箍连接；定频 Rated flow 3.2 m³/h, head 25 m, clamp connection; fixed speed | SS316L | 流动相A / Mobile phase A | 台 / unit | 1 |  |  | 35 |  |  |  |  | 7 |  | BPE管件（HC） / BPE fittings (Hastelloy) | 60 | 11月10 / 10 Nov | [56 empty] | 已订购、哈氏合金货期长 / Ordered; the Hastelloy items have a long lead time | 7 |  | DCS系统供货 / Supply of the DCS system | 45 | 10月31 / 31 Oct | [79 empty] | 未订购，预估到货时间 / Not ordered yet, estimated delivery date | bar: 10月 / October 10 to 10月 / October 31
10 | 1211-HPPC03-AT09-P01 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：12.5m3/h 扬程：25m 卡箍连接；变频 Rated flow 12.5 m³/h, head 25 m, clamp connection; variable speed | SS316L | 流动相B / Mobile phase B | 台 / unit | 1 | 新采购 / Newly purchased |  | 35 |  |  |  |  | 8 | 现场改造 / On-site modification | 钢平台主框架搭建 / Erection of the main steel platform frame | 5 | [57 empty] | 设备到货前提前施工 / Carry out the work before the equipment arrives | 8 | 现场改造 / On-site modification | BPE管件（HC） / BPE fittings (Hastelloy) | 60 | 11月10 / 10 Nov | [79 empty] | 已订购、哈氏合金货期长 / Ordered; the Hastelloy items have a long lead time | bar: 10月 / October 10 to 11月 / November 10
11 | 1211-HPPC03-AT11-P01 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：12.5m3/h 扬程：25m 卡箍连接；变频 Rated flow 12.5 m³/h, head 25 m, clamp connection; variable speed | SS316L | 纯化水 / Purified water | 台 / unit | 1 | 新采购 / Newly purchased |  | 35 |  |  |  |  | 9 |  | 彩钢板拆除、外墙拆除 / Removal of sandwich panels and the external wall | 2 | [58 empty] | 9 |  | 钢平台主框架搭建 / Erection of the main steel platform frame | 5 | [80 empty] | 设备到货前提前施工 / Carry out the work before the equipment arrives | bar: 10月 / October 10 to 10月 / October 14
12 | 1211-HPPC03-AT10-P01 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：3.2m3/h 扬程：25m 卡箍连接；定频 Rated flow 3.2 m³/h, head 25 m, clamp connection; fixed speed | SS316L | 乙腈 / Acetonitrile | 台 / unit | 1 | 新采购 / Newly purchased |  | 35 |  |  |  |  | 11 |  | 钢平台施工、铺板 / Steel platform erection and decking | 5 | [57 empty] | —— | 11 |  | 储罐吊装就位、HC釜吊装 / Lifting the storage tanks into place, lifting the Hastelloy reactor | 2+1 | [80 empty] | 需要等HC釜到货 / Waiting for delivery of the Hastelloy reactor | bar: 10月 / October 16 to 10月 / October 17; 11月 / November 1
14 | 1211-HPPC03-AT07-P02 | 卫生级气动隔膜泵 / Sanitary pneumatic diaphragm pump | 额定流量：5m3/h 扬程：25m 卡箍连接 Rated flow 5 m³/h, head 25 m, clamp connection | SS316L | 废液 / Waste liquid | 台 / unit | 1 | 新采购 / Newly purchased | 利旧车间现货，已完成 / Reuse stock available in the workshop; completed | 0 |  |  |  |  | 12 |  | 外墙恢复、彩钢板恢复 / Reinstatement of the external wall and the sandwich panels | 2 | [57 empty] | —— | 12 |  | 钢平台施工、铺板 / Steel platform erection and decking | 5 | [80 empty] | —— | bar: 10月 / October 18 to 10月 / October 22; 11月 / November 2 to 11月 / November 3
21 | 配件 / Components | 质量流量计（快开、BPE） / Mass flow meter (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 已经订货，待确认到货时间。 / Ordered; delivery date to be confirmed. | 30 |  |  |  | BPE要求 / BPE requirements | 13 |  | 管道安装 / Piping installation | 15 | [57 empty] | —— | 13 |  | 外墙恢复、彩钢板恢复 / Reinstatement of the external wall and the sandwich panels | 2 | [80 empty] | —— | bar: 11月 / November 2 to 11月 / November 3
22 |  | 气动隔膜调节阀（快开、BPE） Pneumatic diaphragm control valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 已经提报流程，待确认到货时间。 The request has been submitted; delivery date to be confirmed. | 42 |  |  |  |  | 14 |  | 电气、仪表安装 / Electrical and instrumentation installation | 10 | [57 empty] | —— | 14 |  | 管道安装 / Piping installation | 15 | [80 empty] | 哈氏合金泵最后替换 / The Hastelloy pumps are replaced last | bar: 10月 / October 22 to 11月 / November 5; 12月 / December 16
23 |  | 气动隔膜开关阀（快开、BPE） Pneumatic diaphragm on/off valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 已经提报流程，待确认到货时间。 The request has been submitted; delivery date to be confirmed. | 42 |  |  |  |  | 15 |  | 地面施工、打胶 / Floor work and sealant application | 5 | [57 empty] | —— | 15 |  | 电气、仪表安装 / Electrical and instrumentation installation | 10 | [80 empty] | —— | bar: 10月 / October 29 to 11月 / November 7
24 |  | 气动调节阀（快开、BPE） / Pneumatic control valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 已经提报流程，待确认到货时间。 The request has been submitted; delivery date to be confirmed. | 42 |  |  |  |  | 16 |  | 哈氏合金釜配管 / Piping of the Hastelloy reactor | 5 | [57 empty] | 需要等哈氏合金件 / Waiting for the Hastelloy parts | 16 |  | 地面施工、打胶 / Floor work and sealant application | 5 | [80 empty] | —— | bar: 11月 / November 8 to 11月 / November 10
25 |  | 气动开关阀（快开、BPE） / Pneumatic on/off valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 已经提报流程，待确认到货时间。 The request has been submitted; delivery date to be confirmed. | 42 |  |  |  |  | 17 | 验证 / Qualification | 调试 / Commissioning | [58 empty] | 验证IQ与安装同步执行，打点结束后关闭IQ，IQ在程序调试阶段完成 IQ runs in parallel with installation; IQ is closed after the loop check and is completed during software commissioning | 17 |  | 哈氏合金釜配管 / Piping of the Hastelloy reactor | 5 | [80 empty] | 需要等哈氏合金件 / Waiting for the Hastelloy parts | bar: 11月 / November 11 to 11月 / November 15
26 |  | 雷达液位计 / Radar level transmitter | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 已经提报流程，待确认到货时间。 The request has been submitted; delivery date to be confirmed. | 20 |  |  |  |  | 18 |  | 打点 / Loop check | [58 empty] | —— | 18 | 验证 / Qualification | 调试 / Commissioning
27 |  | 音叉 / Tuning-fork level switch | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 已经提报流程，待确认到货时间。 The request has been submitted; delivery date to be confirmed. | 20 |  |  |  |  | 19 |  | OQ | [58 empty] | —— | 19 |  | 打点 / Loop check | bar: 11月 / November 11 to 11月 / November 12
28 |  | 温度 / Temperature instrument | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 已经提报流程，待确认到货时间。 The request has been submitted; delivery date to be confirmed. | 20 |  |  |  |  | 20 |  | PQ | [58 empty] | —— | 20 |  | OQ | bar: 11月 / November 21 to 11月 / November 24
29 |  | PH / pH instrument | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 已经提报流程，待确认到货时间。 The request has been submitted; delivery date to be confirmed. | 42 |  |  |  |  | 21 | 设备准备 / Equipment preparation | 清洗 / Cleaning | [58 empty] | —— | 21 |  | PQ | bar: 11月 / November 25 to 11月 / November 26
30 |  | 压力 / Pressure instrument | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 已经提报流程，待确认到货时间。 The request has been submitted; delivery date to be confirmed. | 21 | [66 empty] | 22 | 设备准备 / Equipment preparation | 清洗 / Cleaning | bar: 11月 / November 27 to 11月 / November 28
31 |  | 手动隔膜阀 / Manual diaphragm valve | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 已经提报流程，待确认到货时间。 The request has been submitted; delivery date to be confirmed. | 45 | [66 empty] | 23 | 增补验证 / Supplementary qualification | 增补IQ（材质、铭牌、PID） Supplementary IQ (materials, nameplates, P&ID) |  |  | 12月 / December 17: 不占时间 / No additional time needed
32 |  | BPE管道、管件 / BPE piping and fittings | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 已经提报流程，待确认到货时间。 The request has been submitted; delivery date to be confirmed. | 35 |  |  |  |  | 制备组分接收改造-更换泵（316L）、BPE管道（316L）；问题：现场储罐为自行改造的TC口，需要征求客户意见； Retrofit of the fraction receiving area – replace the pumps (316L) and the BPE piping (316L). Open point: the TC connections on the existing site tanks were made in-house, so the customer's opinion is needed. | [61 empty] | 24 |  | 调试(泵、程序调试) / Commissioning (pumps, software) | bar: 12月 / December 17 to 12月 / December 18
[15 empty] | 序号 / No. | 工序 / Activity | 设备/材料 / Equipment / material | 货期/工期 / Lead time / duration | 预计到货时间 / Expected delivery date | 10月 / October | [11 empty] | 11月 / November | [29 empty] | 12月 / December | [13 empty] | 备注 / Remarks | 25 |  | OQ（保压试密、泵流速精度） / OQ (pressure-hold leak test, pump flow accuracy) | bar: 12月 / December 19
[20 empty] | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 |  | 26 |  | PQ（配液确认） / PQ (solution preparation confirmation)
制备系统-D级区-设备清单-客户需求 Preparation system – Grade D area – equipment list – customer requirements | [14 empty] | 1 | 设备采购 / Equipment procurement | 离心泵到货（316） / Delivery of the centrifugal pumps (316L) | 42 | 10月25 / 25 Oct | [56 empty] | 未订购，预估到货时间 / Not ordered yet, estimated delivery date | 27 | 设备准备 / Equipment preparation | 清洗 / Cleaning | bar: 10月 / October 20 to 10月 / October 25
序号 / No. | 设备位号 / Equipment tag | 设备名称 / Equipment name | 技术参数 / Technical parameters | 设备材质 / Equipment material | 使用介质 / Process medium | 单位 / Unit | 数量 / Quantity | 方案 / Option |  | 改造需求 / Modification requirement | 采购周期 / Procurement lead time | 安装周期 / Installation duration | 验证周期 / Qualification duration | 总计时间 / Total time | 2 |  | 自控阀门/仪表采购（316） / Procurement of control valves / instruments (316L) | 42 | 10月25 / 25 Oct | [56 empty] | 部分已订购、部分未订购，预估到货时间 Partly ordered, partly not ordered; estimated delivery date | bar: 10月 / October 20 to 10月 / October 25
1 | 1211-HPPC03-AT03 | 组分接收搅拌罐（带夹套） / Fraction receiving agitated vessel (jacketed) | 1、有效容积8000L； 1. Working volume 8000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：316L不锈钢； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— | 设备材料到货后施工15天 / 15 days of installation work after the equipment and materials arrive | 3d | 21d | 3 |  | BPE管件采购（316） / Procurement of BPE fittings (316L) | 30 | 10月15 / 15 Oct | [56 empty] | 已订购 / Ordered | bar: 10月 / October 20
2 | 1211-HPPC03-AT04/AT05 | 组分接收搅拌罐（带夹套） / Fraction receiving agitated vessel (jacketed) | 1、有效容积3000L； 1. Working volume 3000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：316L不锈钢； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂等 / Various organic solvents | 台 / unit | 2 | 现有已安装设备 / Existing installed equipment | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— |  |  |  | 4 |  | BPE手动阀门（316） / BPE manual valves (316L) | 30 | 10月15 / 15 Oct | [56 empty] | 已订购 / Ordered | bar: 10月 / October 20
3 | 1211-HPPC03-AT06 | 样品搅拌罐（带夹套） / Sample agitated vessel (jacketed) | 1、有效容积1000L； 1. Working volume 1000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：316L不锈钢； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— |  |  |  | 5 | 现场改造 / On-site modification | 现有泵及管道拆除 / Removal of the existing pumps and piping | 1 | [57 empty] | —— | bar: 10月 / October 20
4 | 1211-HPPC03-T06 | 顶样搅拌罐（带夹套） / Top-fraction sample agitated vessel (jacketed) | 1、有效容积1000L； 1. Working volume 1000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：316L不锈钢； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— |  |  |  | 6 |  | 新泵及BPE管道更换 / Replacement with new pumps and BPE piping | 15 | [57 empty] | —— | bar: 10月 / October 21 to 11月 / November 4
5 | *** | 组分接收储罐（不带夹套） / Fraction receiving storage tank (non-jacketed) | 有效容积100L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 100 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 12 | 现有已安装设备 / Existing installed equipment | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— |  |  |  | 1 |  | 自控阀门/仪表采购（316） / Procurement of control valves / instruments (316L) | 42 | 10月25 / 25 Oct | 12月 / December 1: 部分已订购、部分未订购，预估到货时间 Partly ordered, partly not ordered; estimated delivery date
| 1211-HPPC03-AT03-P01 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：12.5m3/h 扬程：25m 卡箍连接 变频 Rated flow 12.5 m³/h, head 25 m, clamp connection, variable speed | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 需新采购 / New purchase required | 确认图纸中，合同今天，明天催促完毕，预计10月中下旬到货。 Drawings are being confirmed; the contract will be chased today and tomorrow; delivery is expected in the second half of October. | 35 |  |  |  |  | 2 |  | BPE管件采购（316） / Procurement of BPE fittings (316L) | 30 | 10月15 / 15 Oct | 12月 / December 1: 已订购 / Ordered
| 1211-HPPC03-AT03-P02 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：2m3/h 扬程：20m 卡箍连接 定频 Rated flow 2 m³/h, head 20 m, clamp connection, fixed speed | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 需新采购 / New purchase required | 确认图纸中，合同今天，明天催促完毕，预计10月中下旬到货。 Drawings are being confirmed; the contract will be chased today and tomorrow; delivery is expected in the second half of October. | 35 |  |  |  |  | 3 |  | BPE手动阀门（316） / BPE manual valves (316L) | 30 | 10月15 / 15 Oct | 12月 / December 1: 已订购 / Ordered
| 1211-HPPC03-AT04-P01 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：12.5m3/h 扬程：25m 卡箍连接 变频 Rated flow 12.5 m³/h, head 25 m, clamp connection, variable speed | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 需新采购 / New purchase required | 确认图纸中，合同今天，明天催促完毕，预计10月中下旬到货。 Drawings are being confirmed; the contract will be chased today and tomorrow; delivery is expected in the second half of October. | 35 |  |  |  |  | 4 |  | BPE管道更换 / Replacement of BPE piping | 5 | bar: 10月 / October 23 to 10月 / October 27; 12月 / December 1
| 1211-HPPC03-AT05-P01 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：12.5m3/h 扬程：25m 卡箍连接 变频 Rated flow 12.5 m³/h, head 25 m, clamp connection, variable speed | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 需新采购 / New purchase required | 确认图纸中，合同今天，明天催促完毕，预计10月中下旬到货。 Drawings are being confirmed; the contract will be chased today and tomorrow; delivery is expected in the second half of October. | 35 |  |  |  |  | 5 |  | 电气、仪表安装 / Electrical and instrumentation installation | 3 | bar: 10月 / October 25 to 10月 / October 27; 12月 / December 1
| 1211-HPPC03-AT06-P01 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：12.5m3/h 扬程：25m 卡箍连接 变频 Rated flow 12.5 m³/h, head 25 m, clamp connection, variable speed | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 需新采购 / New purchase required | 确认图纸中，合同今天，明天催促完毕，预计10月中下旬到货。 Drawings are being confirmed; the contract will be chased today and tomorrow; delivery is expected in the second half of October. | 35 |  |  |  |  | 6 |  | 空调 / HVAC |  |  | 10月 / October 28: 涉及动火需要做一静一动5天培养 Hot work is involved, so one at-rest and one in-operation monitoring run with 5-day incubation is required; 12月 / December 1: 验证IQ与安装同步执行 / IQ runs in parallel with installation
| 1211-HPPC03-T06-P01 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：3.2m3/h 扬程：25m 卡箍连接 定频 Rated flow 3.2 m³/h, head 25 m, clamp connection, fixed speed | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 需新采购 / New purchase required | 确认图纸中，合同今天，明天催促完毕，预计10月中下旬到货。 Drawings are being confirmed; the contract will be chased today and tomorrow; delivery is expected in the second half of October. | 35 |  |  |  |  | 7 |  | 储罐、管路 / Storage tanks and piping | bar: 10月 / October 29 to 11月 / November 2; 12月 / December 1
6 | *** | 气动隔膜泵 / Pneumatic diaphragm pump | 5m³/h，25m，快开连接 / 5 m³/h, 25 m, quick-connect | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 2 | 现有已安装设备 / Existing installed equipment | 现有已安装设备 / Existing installed equipment | 匀浆罐进料及出料 / Charging and discharging of the homogenisation vessel | 35天 / 35 days |  |  |  | 8 |  | 清洗 / Cleaning | bar: 11月 / November 3 to 11月 / November 4
| *** | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：2m3/h 扬程：20m 卡箍连接 定频 Rated flow 2 m³/h, head 20 m, clamp connection, fixed speed | SS316L | 合格组分 / In-spec fractions | 台 / unit | 1 |  | 确认图纸中，合同今天，明天催促完毕，预计10月中下旬到货。 Drawings are being confirmed; the contract will be chased today and tomorrow; delivery is expected in the second half of October. | 35
| *** | 气动隔膜泵 / Pneumatic diaphragm pump | 额定流量：5m3/h 扬程：25m 卡箍连接 Rated flow 5 m³/h, head 25 m, clamp connection | SS316L | 不合格组分 / Out-of-spec fractions | 台 / unit | 1 | [7 empty] | 序号 / No. | 工序 / Activity | 设备/材料 / Equipment / material | 货期/工期 / Lead time / duration | 预计到货时间 / Expected delivery date | 10月 / October 20: 10月 / October; 11月 / November 1: 11月 / November; 12月 / December 1: 12月 / December | 备注 / Remarks
7 | 配件 / Components | 质量流量计（快开、BPE） / Mass flow meter (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 已经提报流程，待确认到货时间。 The request has been submitted; delivery date to be confirmed. | 可满足 / Acceptable | —— | [8 empty] | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
8 |  | 气动隔膜调节阀（快开、BPE） Pneumatic diaphragm control valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 已经提报流程，待确认到货时间。 The request has been submitted; delivery date to be confirmed. | 采购快开调节阀 / Purchase quick-connect control valves | 42天 / 42 days |  |  |  | 1 | 设备采购 / Equipment procurement | 自控阀门/仪表采购（316） / Procurement of control valves / instruments (316L) | 42 | 10月25 / 25 Oct | [56 empty] | 部分已订购、部分未订购，预估到货时间 Partly ordered, partly not ordered; estimated delivery date | bar: 10月 / October 20 to 10月 / October 25
9 |  | 气动隔膜开关阀（快开、BPE） Pneumatic diaphragm on/off valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 已经提报流程，待确认到货时间。 The request has been submitted; delivery date to be confirmed. | 采购快开开关阀 / Purchase quick-connect on/off valves | 42天 / 42 days |  |  |  | 2 |  | BPE管件采购（316） / Procurement of BPE fittings (316L) | 30 | 10月15 / 15 Oct | [56 empty] | 已订购 / Ordered | bar: 10月 / October 20
10 |  | 气动调节阀（快开、BPE） / Pneumatic control valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 已经提报流程，待确认到货时间。 The request has been submitted; delivery date to be confirmed. | 采购快开调节阀 / Purchase quick-connect control valves | 35天 / 35 days |  |  |  | 3 |  | BPE手动阀门（316） / BPE manual valves (316L) | 30 | 10月15 / 15 Oct | [56 empty] | 已订购 / Ordered | bar: 10月 / October 20
11 |  | 气动开关阀（快开、BPE） / Pneumatic on/off valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 已经提报流程，待确认到货时间。 The request has been submitted; delivery date to be confirmed. | 采购快开开关阀 / Purchase quick-connect on/off valves | 35天 / 35 days |  |  |  | 4 | 现场改造 / On-site modification | BPE管道更换 / Replacement of BPE piping | 5 | [57 empty] | —— | bar: 10月 / October 23 to 10月 / October 27
12 |  | 雷达液位计 / Radar level transmitter | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 已经提报流程，待确认到货时间。 The request has been submitted; delivery date to be confirmed. |  | —— |  |  |  | 5 |  | 电气、仪表安装 / Electrical and instrumentation installation | 3 | [57 empty] | —— | bar: 10月 / October 25 to 10月 / October 27
13 |  | 音叉 / Tuning-fork level switch | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 已经提报流程，待确认到货时间。 The request has been submitted; delivery date to be confirmed. |  | —— |  |  |  | 6 | 验证 / Qualification | 空调 / HVAC |  |  | 10月 / October 28: 涉及动火需要做一静一动5天培养 Hot work is involved, so one at-rest and one in-operation monitoring run with 5-day incubation is required | 验证IQ与安装同步执行 / IQ runs in parallel with installation
14 |  | 温度 / Temperature instrument | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 已经提报流程，待确认到货时间。 The request has been submitted; delivery date to be confirmed. |  | —— | 安装周期 / Installation duration | 验证周期 / Qualification duration | 总计时间 / Total time | 7 |  | 增补验证 / Supplementary qualification | [58 empty] | —— | bar: 10月 / October 29 to 11月 / November 2
15 |  | PH / pH instrument | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 已经提报流程，待确认到货时间。 The request has been submitted; delivery date to be confirmed. |  | —— | 管件到货后施工预计5天 / Around 5 days of installation work after the fittings arrive | 3d | 11d | 8 | 设备准别 / Equipment preparation | 清洗 / Cleaning | bar: 11月 / November 3 to 11月 / November 4
16 |  | 压力 / Pressure instrument | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 已经提报流程，待确认到货时间。 The request has been submitted; delivery date to be confirmed. |  | ——
17 |  | 手动隔膜阀 / Manual diaphragm valve | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 已经提报流程，待确认到货时间。 The request has been submitted; delivery date to be confirmed. |  | ——
18 |  | BPE管道、管件 / BPE piping and fittings | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 已经提报流程，待确认到货时间。 The request has been submitted; delivery date to be confirmed. | 整体按照BPE的管路替换，满足2D，排尽等4类管路需求 The piping is replaced entirely to BPE standard, meeting the 2D and drainability requirements for Category 4 piping | BPE管件28天；BPE阀门42天 BPE fittings 28 days; BPE valves 42 days
超滤系统设备清单-自己评估 / Ultrafiltration system equipment list – internal assessment | [14 empty] | 沉淀区改造-更换80L储罐（316L）、BPE管道（316L）；问题：现场设备（釜、三合一、储罐）为自行改造的TC口，需要征求客户意见； Retrofit of the precipitation area – replace the 80 L storage tank (316L) and the BPE piping (316L). Open point: the TC connections on the existing site equipment (reactor, filter-dryer, storage tanks) were made in-house, so the customer's opinion is needed.
序号 / No. | 设备位号 / Equipment tag | 设备名称 / Equipment name | 技术参数 / Technical parameters | 设备材质 / Equipment material | 使用介质 / Process medium | 单位 / Unit | 数量 / Quantity | 方案 / Option | 09/17/2026进展 / Status as of 09/17/2026 | 改造需求 / Modification requirement | 采购周期 / Procurement lead time |  |  |  | 序号 / No. | 工序 / Activity | 设备/材料 / Equipment / material | 货期/工期 / Lead time / duration | 预计到货时间 / Expected delivery date | 10月 / October 20: 10月 / October; 11月 / November 1: 11月 / November; 12月 / December 1: 12月 / December | 备注 / Remarks
1 | 1211-TFF01-T01 | 超滤接收储罐（带夹套） / Ultrafiltration receiving storage tank (jacketed) | 1、有效容积1000L； 1. Working volume 1000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | 可满足 / Acceptable | —— | [8 empty] | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
2 | 配件 / Components | 质量流量计（快开、BPE） / Mass flow meter (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | 可满足 / Acceptable | —— | 安装周期 / Installation duration | 验证周期 / Qualification duration | 总计时间 / Total time | 1 | 设备采购 / Equipment procurement | YD储罐到货（316） / Delivery of the YD storage tanks (316L) | 40 | 10月20 / 20 Oct | [56 empty] | 已订购 / Ordered | bar: 10月 / October 20
3 |  | 气动隔膜调节阀（快开、BPE） Pneumatic diaphragm control valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | 可满足 / Acceptable | —— | 设备材料到货后施工15天 / 15 days of installation work after the equipment and materials arrive |  |  | 2 |  | 离心泵到货（316） / Delivery of the centrifugal pumps (316L) | 42 | 10月25 / 25 Oct | [56 empty] | 未订购，预估到货时间 / Not ordered yet, estimated delivery date | bar: 10月 / October 20 to 10月 / October 25
4 |  | 气动隔膜开关阀（快开、BPE） Pneumatic diaphragm on/off valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | 可满足 / Acceptable | —— |  | 方案一：3d Option 1: 3 d 方案二：7d Option 2: 7 d | 方案一：21dd Option 1: 21 d 方案二：25d Option 2: 25 d | 3 |  | 自控阀门/仪表采购（316） / Procurement of control valves / instruments (316L) | 42 | 10月25 / 25 Oct | [56 empty] | 部分已订购、部分未订购，预估到货时间 Partly ordered, partly not ordered; estimated delivery date | bar: 10月 / October 20 to 10月 / October 25
5 |  | 手动隔膜阀 / Manual diaphragm valve | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | 可满足 / Acceptable | —— |  |  |  | 4 |  | BPE管件采购（316） / Procurement of BPE fittings (316L) | 30 | 10月15 / 15 Oct | [56 empty] | 已订购 / Ordered | bar: 10月 / October 20
6 |  | BPE管道、管件 / BPE piping and fittings | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 已经提报流程，待确认到货时间。 The request has been submitted; delivery date to be confirmed. | 评估甲醇、乙腈水、氢氧化钠溶液是否需要更换为BPE管路。 Assess whether the methanol, acetonitrile / water and sodium hydroxide solution lines have to be changed to BPE piping. | BPE管件28天；BPE阀门42天 BPE fittings 28 days; BPE valves 42 days |  |  |  | 5 |  | BPE手动阀门（316） / BPE manual valves (316L) | 30 | 10月15 / 15 Oct | [56 empty] | 已订购 / Ordered | bar: 10月 / October 20
| *** | 气动隔膜泵 / Pneumatic diaphragm pump | 额定流量：5m3/h 扬程：25m 卡箍连接 Rated flow 5 m³/h, head 25 m, clamp connection | SS316L |  | 台 / unit | 1 |  | 可满足 / Acceptable | [5 empty] | 6 |  | 80L罐拆/装、湿氮气安装 / Removal / installation of the 80 L vessel, installation of the wet nitrogen supply | 1 | [57 empty] | 需要等储罐到货 / Waiting for delivery of the storage tanks | bar: 10月 / October 21
| TJ4S-1211-TFF02-WTK01-MP01 | 离心泵 / Centrifugal pump | 额定流量：3.2m3/h 扬程：20m Rated flow 3.2 m³/h, head 20 m | 304 |  | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable |  |  |  | 15d | 33d | 7 |  | 泵及BPE管道更换 / Replacement of pumps and BPE piping | 15 | [57 empty] | —— | bar: 10月 / October 21 to 11月 / November 4
| TJ4S-1211-TFF02-WTK01-MP02 | 离心泵 / Centrifugal pump | 额定流量：3.2m3/h 扬程：20m Rated flow 3.2 m³/h, head 20 m | 304 |  | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable |  |  |  | - | - | 8 |  | 电气、仪表安装 / Electrical and instrumentation installation | 7 | [57 empty] | —— | bar: 10月 / October 29 to 11月 / November 4
沉淀釜区设备清单-自己评估 / Precipitation reactor area equipment list – internal assessment | [14 empty] | 9 | 验证 / Qualification | 空调 / HVAC |  |  | 11月 / November 5: 涉及动火需要做一静一动5天培养 Hot work is involved, so one at-rest and one in-operation monitoring run with 5-day incubation is required | 验证IQ与安装同步执行 / IQ runs in parallel with installation
序号 / No. | 设备位号 / Equipment tag | 设备名称 / Equipment name | 技术参数 / Technical parameters | 设备材质 / Equipment material | 使用介质 / Process medium | 单位 / Unit | 数量 / Quantity | 方案 / Option |  | 改造需求 / Modification requirement | 采购周期 / Procurement lead time |  |  |  | 10 |  | 增补验证 / Supplementary qualification | [58 empty] | —— | bar: 11月 / November 6 to 11月 / November 10
1 | 1211-R01 | 析晶釜 / Crystallizer | 1、有效容积2000L； 1. Working volume 2000 L; 2、釜内设计温度-25~200℃，夹套设计温度-25~220℃； 2. Reactor design temperature −25 to 200 °C, jacket design temperature −25 to 220 °C; 3、釜内设计压力-0.1~0.4MPa；夹套工作压力0.6Mpa； 3. Reactor design pressure −0.1 to 0.4 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：304不锈钢衬C22或C276； Product contact: 304 stainless steel lined with C22 or C276; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、酸、碱等 / Various organic solvents, acids, bases, etc. | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment | 现有已安装设备 / Existing installed equipment | 可满足 / Acceptable | —— |  |  |  | 11 | 设备准别 / Equipment preparation | 清洗 / Cleaning | bar: 11月 / November 11 to 11月 / November 12
3 | 1211-AT01 | 搅拌罐 / Agitated vessel | 1、有效容积600L； 1. Working volume 600 L; 2、罐内设计温度-25~200℃，夹套设计温度-25~220℃； 2. Vessel design temperature −25 to 200 °C, jacket design temperature −25 to 220 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：316L不锈钢； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、盐溶液等 / Various organic solvents, salt solutions, etc. | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment | 现有已安装设备 / Existing installed equipment | 管路需要满足BPE标准，按照4类管路进行改造。 The piping has to meet the BPE standard and is modified to the Category 4 piping requirements. 管线、排尽不满足2D Piping and drainability do not meet 2D | BPE管件28天；BPE阀门42天 BPE fittings 28 days; BPE valves 42 days |  | 3d | 21d
4 | 1211-AT02 | 搅拌罐 / Agitated vessel | 1、有效容积80L； 1. Working volume 80 L; 2、罐内设计温度-25~200℃，夹套设计温度-25~220℃； 2. Vessel design temperature −25 to 200 °C, jacket design temperature −25 to 220 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：316L不锈钢； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、酸、碱等 / Various organic solvents, acids, bases, etc. | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment | 现有已安装设备 / Existing installed equipment | 下口存在法兰，需要进行改造。滴加碱液的管路确认需要更换BPE管路。 There is a flange at the bottom outlet that has to be modified. It is confirmed that the caustic dosing line has to be changed to BPE piping. | 方案一：使用英德现货改造40天；（前提是制备配盐罐不换） Option 1: modify a Yingde stock tank, 40 days (provided the salt preparation vessel is not replaced) 方案二：现场为哈氏合金材质，改造材料需要60天；涉及压力容器改造； Option 2: the existing unit is Hastelloy, so the modification material takes 60 days; a pressure-vessel modification is involved
| TJ4S-1211-AT02-P02 | 气动隔膜泵 / Pneumatic diaphragm pump | 额定流量：5m3/h 扬程：25m 卡箍连接 Rated flow 5 m³/h, head 25 m, clamp connection | SS316L |  | 台 / unit | 1 |  | 现有已安装设备 / Existing installed equipment
15 | TJ4S-1211-AT01-P01 | 卫生级四元隔膜泵 / Sanitary four-head diaphragm pump | 额定流量：200L/h BPE接口 卡箍连接 Rated flow 200 L/h, BPE connection, clamp connection | 316L |  | 台 / unit | 1 | 需新采购 / New purchase required | 316L已经订货完毕，预计9月底到货，生产郭泽鹏走的流程。 The 316L units are ordered and are expected end of September; the request was raised by Production (Guo Zepeng). 哈氏合金的货期3个月，预计在12月份才能到货，已经下单。 The Hastelloy units have a 3-month lead time and are expected in December; the order is placed. | 采购四元隔膜泵替换 / Purchase replacement four-head diaphragm pumps | ——
16 | TJ4S-1211-AT02-P01 | 卫生级四元隔膜泵 / Sanitary four-head diaphragm pump | 额定流量：20L/h BPE接口 卡箍连接 Rated flow 20 L/h, BPE connection, clamp connection | 316L |  | 台 / unit | 1 | 需新采购 / New purchase required | 316L已经订货完毕，预计9月底到货，生产郭泽鹏走的流程。 The 316L units are ordered and are expected end of September; the request was raised by Production (Guo Zepeng). 哈氏合金的货期3个月，预计在12月份才能到货，已经下单。 The Hastelloy units have a 3-month lead time and are expected in December; the order is placed. |  | ——
5 | 1211-Fd01 | 三合一 / Filter-dryer | 1、设备尺寸DN1200； 1. Equipment size DN1200; 2、罐内设计温度-25~200℃，夹套设计温度-25~220℃； 2. Vessel design temperature −25 to 200 °C, jacket design temperature −25 to 220 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：304不锈钢衬C22或C276； Product contact: 304 stainless steel lined with C22 or C276; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、酸、碱等 / Various organic solvents, acids, bases, etc. | 台 / unit | 1 | 现有已安装设备 / Existing installed equipment | 已完成 / Completed | 可满足 / Acceptable | ——
7 | *** | 旋分筛 / Rotary sifter | 处理量200kg/h. Throughput 200 kg/h. | SS316L | 固体 / Solids | 台 / unit | 1 | 购新安装 / Purchase new and install | 市场上持续寻找中； / Still being sourced on the market; | 市场上持续寻找中； / Still being sourced on the market; | ——
8 | 配件 / Components | 质量流量计（快开、BPE） / Mass flow meter (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 已经提报流程，待确认到货时间。 The request has been submitted; delivery date to be confirmed. | 可满足 / Acceptable | ——
9 |  | 气动隔膜调节阀（快开、BPE） Pneumatic diaphragm control valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 已经提报流程，待确认到货时间。 The request has been submitted; delivery date to be confirmed. | 可满足 / Acceptable | ——
10 |  | 气动隔膜开关阀（快开、BPE） Pneumatic diaphragm on/off valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 已经提报流程，待确认到货时间。 The request has been submitted; delivery date to be confirmed. | 可满足 / Acceptable | BPE管件28天；BPE阀门42天 BPE fittings 28 days; BPE valves 42 days
11 |  | 手动隔膜阀 / Manual diaphragm valve | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 已经提报流程，待确认到货时间。 The request has been submitted; delivery date to be confirmed. | 可满足 / Acceptable
12 |  | BPE管道、管件 / BPE piping and fittings | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 已经提报流程，待确认到货时间。 The request has been submitted; delivery date to be confirmed. | 三合一淋洗管路不是满足BPE； The spray piping of the filter-dryer does not meet BPE; 600L罐管路不满足； the piping of the 600 L vessel does not comply; 管路需要满足BPE标准，按照4类管路进行改造。管线、排尽不满足2D the piping has to meet the BPE standard and is modified to the Category 4 piping requirements. Piping and drainability do not meet 2D
| TJ4S-1211-FD01-Tr01-P01 | 气动隔膜泵 / Pneumatic diaphragm pump | 额定流量：5m3/h 扬程：30m 卡箍连接 Rated flow 5 m³/h, head 30 m, clamp connection | 防腐 / Corrosion-resistant |  | 台 / unit | 1 |  | 已完成 / Completed
| TJ4S-1211-FD01-Tr01-P02 | 气动隔膜泵 / Pneumatic diaphragm pump | 额定流量：5m3/h 扬程：30m 卡箍连接 Rated flow 5 m³/h, head 30 m, clamp connection | 防腐 / Corrosion-resistant |  | 台 / unit | 1 |  | 已完成 / Completed
| TJ4S-1212-FD06-Tr01-P01 | 气动隔膜泵 / Pneumatic diaphragm pump | 额定流量：5m3/h 扬程：30m 卡箍连接 Rated flow 5 m³/h, head 30 m, clamp connection | 防腐 / Corrosion-resistant |  | 台 / unit | 1 |  | 已完成 / Completed
| *** | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：2m3/h 扬程：20m 卡箍连接 定频 Rated flow 2 m³/h, head 20 m, clamp connection, fixed speed | SS316L | 注射水 / Water for injection | 台 / unit | 2 | 需新采购 / New purchase required | 确认图纸中，合同今天，明天催促完毕，预计10月中下旬到货。 Drawings are being confirmed; the contract will be chased today and tomorrow; delivery is expected in the second half of October. | 注射水泵 / Water-for-injection pump

## 方案3 Option 3 All New (hidden)
多肽厂房2现有设备替换-采购清单-只考虑现有设备及管道替换，不考虑其他（如新增CIP等） Peptide Building 2, replacement of existing equipment – purchasing list – covers replacement of existing equipment and piping only, excluding anything else (such as a new CIP system) | [70 empty] | i
制备系统-连续配液-CNC区-设备清单 Preparation system – continuous solution preparation – CNC area – equipment list
序号 / No. | 设备位号 / Equipment tag | 设备名称 / Equipment name | 技术参数 / Technical parameters | 设备材质 / Equipment material | 使用介质 / Process medium | 单位 / Unit | 数量 / Quantity | 设备来源 / Equipment source | 09/17/2026进展 / Status as of 09/17/2026 | 采购周期（天） / Procurement lead time (days) | 安装周期 / Installation duration | 验证周期 / Qualification duration | 总计时间 / Total time | 技术要求 / Technical requirements
1 | 1213-R05 | 哈氏合金反应釜 / Hastelloy reactor | 3000L哈氏合金釜 / 3000 L Hastelloy reactor | C276 | 浓盐溶液 / Concentrated salt solution | 台 / unit | 1 | 新采购 / Newly purchased | 暂未采购 / Not purchased yet | 100 | 30 | 19d(打点2d，程序调试5d+泵调试3d+验证9d) 19 d (loop check 2 d, software commissioning 5 d + pump commissioning 3 d + qualification 9 d) 验证IQ与安装同步执行，打点结束后关闭IQ，IQ在程序调试阶段完成 IQ runs in parallel with installation; IQ is closed after the loop check and is completed during software commissioning |  | 1、设备应满足ASME BPE要求，包括不限于如下要求： 1. The equipment shall comply with ASME BPE, including but not limited to: （1）设备接口采用NA接口，满足2D要求；接口尺寸及数量以确认图纸为准； (1) NA-type connections meeting the 2D drainability requirement; connection sizes and quantities as per the approved drawings; （2）设计淋洗口，需配淋洗球，满足全面清洗且通过核黄素清洗验证； (2) Spray port with spray ball, giving full coverage and passing the riboflavin coverage test; （3）出料口焊接隔膜阀，满足2D要求； (3) Diaphragm valve welded to the outlet, meeting the 2D requirement; （4）外表面抛光粗糙度<0.8um，内壁抛光粗糙度<0.4um； (4) External surface roughness < 0.8 µm, internal surface roughness < 0.4 µm; (5) 设备的原材、配件、生产制造及验收应严格按照ASME BPE要求进行，并提供相关证明资料； (5) Raw materials, components, manufacturing and acceptance strictly in line with ASME BPE, with the supporting documentation provided; 2、电机、减速机要求： 2. Motor and gearbox: （1）采用国内知名品牌；整体外包不锈钢，满足卫生级要求； (1) Well-known domestic brand; fully stainless-steel clad to sanitary standard; （2）防爆等级 ExdIIBT4 Gb，防护等级不低于IP55;电机能效不低于二级； (2) Explosion protection Ex d IIB T4 Gb, ingress protection not lower than IP55; motor efficiency class 2 or better; 3、机封采用双端面卫生级干磨机封，采用国内知名品牌； 3. Double-end sanitary dry-running mechanical seal from a well-known domestic brand; 4、搅拌材质与罐体一直，搅拌形式最终确认图纸为准； 4. Agitator material identical to the vessel; agitator design as per the approved drawings; |  | 制备连续配液系统改造-储罐及泵全部换新（316+HC）、改BPE管道（316+HC） Retrofit of the continuous solution preparation system – replace all storage tanks and pumps with new units (316L + Hastelloy) and convert to BPE piping (316L + Hastelloy)
2 | 1211-HPPC03-AT01 | 配液搅拌罐（不带夹套） / Solution preparation agitated vessel (non-jacketed) | 有效容积500L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 500 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | C22或C276 / C22 or C276 | 浓盐溶液 / Concentrated salt solution | 台 / unit | 1 | 新采购 / Newly purchased | 议价中，暂未确认供应商 / Under price negotiation; supplier not yet confirmed | 100 | [5 empty] | 序号 / No. | 工序 / Activity | 设备/材料 / Equipment / material | 货期/工期 / Lead time / duration | 预计到货时间 / Expected delivery date | 12月 / December | [30 empty] | 01月 / January | [20 empty] | 备注 / Remarks
3 | 1211-HPPC03-AT02 | 配液搅拌罐（不带夹套） / Solution preparation agitated vessel (non-jacketed) | 有效容积500L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 500 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | C22或C276 / C22 or C276 | 浓盐溶液 / Concentrated salt solution | 台 / unit | 1 | 新采购 / Newly purchased | 议价中，暂未确认供应商 / Under price negotiation; supplier not yet confirmed | 100 | [10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
4 | 1211-HPPC03-AT01 | 配液搅拌罐（不带夹套） / Solution preparation agitated vessel (non-jacketed) | 有效容积500L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 500 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 浓盐溶液 / Concentrated salt solution | 台 / unit | 1 | 新采购 / Newly purchased | 议价中，暂未确认供应商 / Under price negotiation; supplier not yet confirmed | 90 | [5 empty] | 1 | 设备采购 / Equipment procurement | 新采购HC搅拌罐到货 / Delivery of the newly purchased Hastelloy agitated vessel | 90 | 12月15 / 15 Dec | [52 empty] | 已订购 / Ordered | bar: 12月 / December 1 to 12月 / December 15
5 | 1211-HPPC03-AT02 | 配液搅拌罐（不带夹套） / Solution preparation agitated vessel (non-jacketed) | 有效容积500L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 500 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 浓盐溶液 / Concentrated salt solution | 台 / unit | 1 | 新采购 / Newly purchased | 议价中，暂未确认供应商 / Under price negotiation; supplier not yet confirmed | 90 | [5 empty] | 2 |  | 新采购储罐到货（316） / Delivery of the newly purchased storage tanks (316L) | 80 | 12月05 / 05 Dec | [52 empty] | 已订购 / Ordered | bar: 12月 / December 1 to 12月 / December 5
6 | 1211-HPPC03-T01 | 纯水储罐（不带夹套） / Purified water storage tank (non-jacketed) | 有效容积1000L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 1000 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 纯化水 / Purified water | 台 / unit | 1 | 新采购 / Newly purchased | 议价中，暂未确认供应商 / Under price negotiation; supplier not yet confirmed | 80 |  |  |  | 设备应满足ASME BPE要求，包括不限于如下要求： The equipment shall comply with ASME BPE, including but not limited to: （1）设备接口采用NA接口，满足2D要求；接口尺寸及数量以确认图纸为准； (1) NA-type connections meeting the 2D drainability requirement; connection sizes and quantities as per the approved drawings; （2）设计淋洗口，需配淋洗球，满足全面清洗且通过核黄素清洗验证； (2) Spray port with spray ball, giving full coverage and passing the riboflavin coverage test; （3）出料口焊接隔膜阀，满足2D要求； (3) Diaphragm valve welded to the outlet, meeting the 2D requirement; （4）外表面抛光粗糙度<0.8um，内壁抛光粗糙度<0.4um； (4) External surface roughness < 0.8 µm, internal surface roughness < 0.4 µm; (5) 设备的原材、配件、生产制造及验收应严格按照ASME BPE要求进行，并提供相关证明资料； (5) Raw materials, components, manufacturing and acceptance strictly in line with ASME BPE, with the supporting documentation provided; |  | 3 |  | 离心泵到货（316） / Delivery of the centrifugal pumps (316L) | 42 | 10月25 / 25 Oct | [52 empty] | 未订购，预估到货时间 / Not ordered yet, estimated delivery date
7 | 1211-HPPC03-T02 | 乙腈储罐（不带夹套） / Acetonitrile storage tank (non-jacketed) | 有效容积1000L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 1000 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 新鲜乙腈、备用 / Fresh acetonitrile, spare | 台 / unit | 2 | 新采购 / Newly purchased | 议价中，暂未确认供应商 / Under price negotiation; supplier not yet confirmed | 80 | [5 empty] | 4 |  | 四元隔膜泵到货（316） / Delivery of the four-head diaphragm pumps (316L) | 25 | 10月10 / 10 Oct | [52 empty] | 已订购 / Ordered
8 | 1211-HPPC03-T03 | 流动相A储罐（不带夹套） / Mobile phase A storage tank (non-jacketed) | 有效容积1000L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 1000 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 流动相A / Mobile phase A | 台 / unit | 1 | 新采购 / Newly purchased | 议价中，暂未确认供应商 / Under price negotiation; supplier not yet confirmed | 80 | [5 empty] | 5 |  | 四元隔膜泵到货（HC） / Delivery of the four-head diaphragm pumps (Hastelloy) | 90 | 12月15 / 15 Dec | [52 empty] | 已订购 / Ordered | bar: 12月 / December 1 to 12月 / December 15
9 | 1211-HPPC03-T04 | 流动相B储罐（不带夹套） / Mobile phase B storage tank (non-jacketed) | 有效容积1000L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 1000 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 流动相B / Mobile phase B | 台 / unit | 1 | 新采购 / Newly purchased | 议价中，暂未确认供应商 / Under price negotiation; supplier not yet confirmed | 80 | [5 empty] | 6 |  | 自控阀门/仪表采购（316） / Procurement of control valves / instruments (316L) | 42 | 10月25 / 25 Oct | [52 empty] | 部分已订购、部分未订购，预估到货时间 Partly ordered, partly not ordered; estimated delivery date
10 | 1211-HPPC03-T05 | 甲醇储罐（不带夹套） / Methanol storage tank (non-jacketed) | 有效容积1000L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 1000 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 甲醇 / Methanol | 台 / unit | 1 | 新采购 / Newly purchased | 议价中，暂未确认供应商 / Under price negotiation; supplier not yet confirmed | 80 | [5 empty] | 7 |  | BPE管件采购（316） / Procurement of BPE fittings (316L) | 30 | 10月15 / 15 Oct | [52 empty] | 已订购 / Ordered
10 | 1211-HPPC03-T03-P01 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：2.5m3/h 扬程：25m 卡箍连接 Rated flow 2.5 m³/h, head 25 m, clamp connection | SS316L | 流动相A / Mobile phase A | 台 / unit | 1 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2 |  |  |  |  | 设备应满足ASME BPE要求，包括不限于如下要求： The equipment shall comply with ASME BPE, including but not limited to: （1）设备接口采用NA接口，满足2D要求，设备腔体可排净； (1) NA-type connections meeting the 2D drainability requirement, with a fully drainable equipment body; （2）外表面抛光粗糙度<0.8um，内壁抛光粗糙度<0.4um； (2) External surface roughness < 0.8 µm, internal surface roughness < 0.4 µm; （3）设备的原材、配件、生产制造及验收应严格按照ASME BPE要求进行，并提供相关证明资料； (3) Raw materials, components, manufacturing and acceptance strictly in line with ASME BPE, with the supporting documentation provided; |  | 8 |  | BPE管件（HC） / BPE fittings (Hastelloy) | 60 | 11月10 / 10 Nov | [52 empty] | 已订购 / Ordered
11 | 1211-HPPC03-T03-P02 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：3.2m3/h 扬程：25m 卡箍连接 定频 Rated flow 3.2 m³/h, head 25 m, clamp connection, fixed speed | SS316L | 流动相B / Mobile phase B | 台 / unit | 1 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2 | [6 empty] | 9 | 现场改造 / On-site modification | 储罐拆除 / Storage tank removal | 3 | [53 empty] | 提前切割罐口 / Cut the vessel nozzles in advance | bar: 12月 / December 3 to 12月 / December 5
12 | 1211-HPPC03-T04-P01 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：2.5m3/h 扬程：25m 卡箍连接 Rated flow 2.5 m³/h, head 25 m, clamp connection | SS316L | 流动相B/新鲜乙腈 / Mobile phase B / fresh acetonitrile | 台 / unit | 1 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2 | [6 empty] | 10 |  | 储罐安装 / Storage tank installation | 2 | [53 empty] | 需要等HC件到货 / Waiting for delivery of the Hastelloy parts | bar: 12月 / December 6; 12月 / December 16
13 | 1211-HPPC03-WT01-P01 | 离心泵 / Centrifugal pump | 额定流量：3.2m3/h 扬程：20m 卡箍连接 Rated flow 3.2 m³/h, head 20 m, clamp connection | 304 | 制备废液 / Preparation waste liquid | 台 / unit | 1 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2 | [6 empty] | 11 |  | 泵及BPE管道安装 / Installation of pumps and BPE piping | 20 | [53 empty] | 需要等储罐到货 / Waiting for delivery of the storage tanks | bar: 12月 / December 7 to 12月 / December 26
14 | 1211-HPPC03-WT02-P01 | 离心泵 / Centrifugal pump | 额定流量：3.2m3/h 扬程：20m 卡箍连接 Rated flow 3.2 m³/h, head 20 m, clamp connection | 304 | 制备废液 / Preparation waste liquid | 台 / unit | 1 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2 | [6 empty] | 12 |  | 电气、仪表安装 / Electrical and instrumentation installation | 10 | [53 empty] | —— | bar: 12月 / December 18 to 12月 / December 27
15 | 1211-HPPC03-AT01-P01 | 卫生级四元隔膜泵 / Sanitary four-head diaphragm pump | 额定流量：3.0Lmin BPE接口 卡箍连接 Rated flow 3.0 L/min, BPE connection, clamp connection | 316L或C276 / 316L or C276 | 浓盐溶液 / Concentrated salt solution | 台 / unit | 1 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2 | [6 empty] | 13 |  | 地面施工、打胶 / Floor work and sealant application | 5 | [53 empty] | —— | bar: 12月 / December 28 to 01月 / January 1
16 | 1211-HPPC03-AT02-P01 | 卫生级四元隔膜泵 / Sanitary four-head diaphragm pump | 额定流量：2.0Lmin BPE接口 卡箍连接 Rated flow 2.0 L/min, BPE connection, clamp connection | 316L或C276 / 316L or C276 | 浓盐溶液 / Concentrated salt solution | 台 / unit | 1 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2 | [6 empty] | 14 | 验证 / Qualification | 调试 / Commissioning | [54 empty] | 验证IQ与安装同步执行，打点结束后关闭IQ，IQ在程序调试阶段完成 IQ runs in parallel with installation; IQ is closed after the loop check and is completed during software commissioning | bar: 01月 / January 4 to 01月 / January 8
17 | 1211-HPPC03-T01-P01 | 卫生级四元隔膜泵 / Sanitary four-head diaphragm pump | 额定流量：35Lmin BPE接口 卡箍连接 Rated flow 35 L/min, BPE connection, clamp connection | SS316L | 纯化水 / Purified water | 台 / unit | 1 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2 | [6 empty] | 15 |  | 打点 / Loop check | [54 empty] | —— | bar: 01月 / January 2 to 01月 / January 3
18 | 1211-HPPC03-T01-P02 | 卫生级四元隔膜泵 / Sanitary four-head diaphragm pump | 额定流量：3.0Lmin BPE接口 卡箍连接 Rated flow 3.0 L/min, BPE connection, clamp connection | SS316L | 纯化水 / Purified water | 台 / unit | 1 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2 | [6 empty] | 16 |  | OQ | [54 empty] | —— | bar: 01月 / January 9 to 01月 / January 12
19 | 1211-HPPC03-T02-P01 | 卫生级四元隔膜泵 / Sanitary four-head diaphragm pump | 额定流量：5.0Lmin BPE接口 卡箍连接 Rated flow 5.0 L/min, BPE connection, clamp connection | SS316L | 新鲜乙腈 / Fresh acetonitrile | 台 / unit | 1 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2 | [6 empty] | 17 |  | PQ | [54 empty] | —— | bar: 01月 / January 13 to 01月 / January 14
20 | 1211-HPPC03-T02-P02 | 卫生级四元隔膜泵 / Sanitary four-head diaphragm pump | 额定流量：35Lmin BPE接口 卡箍连接 Rated flow 35 L/min, BPE connection, clamp connection | SS316L | 新鲜乙腈 / Fresh acetonitrile | 台 / unit | 1 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2 | [6 empty] | 18 | 设备准备 / Equipment preparation | 清洗 / Cleaning | [54 empty] | —— | bar: 01月 / January 15 to 01月 / January 16
| TJ4S-1213-R05-P01 | 卫生级四元隔膜泵 / Sanitary four-head diaphragm pump | 额定流量：35Lmin BPE接口 卡箍连接 Rated flow 35 L/min, BPE connection, clamp connection | 316L或C276 / 316L or C276 | 浓盐溶液 / Concentrated salt solution | 台 / unit | 1 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2 |  |  |  |  | BPE要求 / BPE requirements
22 | 配件 / Components | 质量流量计（快开、BPE） / Mass flow meter (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 30
23 |  | 气动隔膜调节阀（快开、BPE） Pneumatic diaphragm control valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 42 | [5 empty] | 制备组分接收罐改造-储罐及泵全部换新（316L）、改BPE管道（316L） Retrofit of the fraction receiving vessels – replace all storage tanks and pumps with new units (316L) and convert to BPE piping (316L)
24 |  | 气动隔膜开关阀（快开、BPE） Pneumatic diaphragm on/off valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 42 | [5 empty] | 序号 / No. | 工序 / Activity | 设备/材料 / Equipment / material | 货期/工期 / Lead time / duration | 预计到货时间 / Expected delivery date | 12月 / December 1: 12月 / December; 12月 / December 25: 01月 / January | 备注 / Remarks
25 |  | 气动调节阀（快开、BPE） / Pneumatic control valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 42 | [10 empty] | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 27 | 28 | 29 | 30 | 31
26 |  | 气动开关阀（快开、BPE） / Pneumatic on/off valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 42 | [5 empty] | 1 | 设备采购 / Equipment procurement | 搅拌储罐采购到货 / Delivery of the purchased agitated storage tanks | 90 | 12月15 / 15 Dec | [52 empty] | 未订购，预估到货时间 / Not ordered yet, estimated delivery date | bar: 12月 / December 8 to 12月 / December 15
27 |  | 雷达液位计 / Radar level transmitter | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 20 | [5 empty] | 2 |  | 离心泵到货（316） / Delivery of the centrifugal pumps (316L) | 42 | 10月25 / 25 Oct | [52 empty] | 部分已订购、部分未订购，预估到货时间 Partly ordered, partly not ordered; estimated delivery date
28 |  | 音叉 / Tuning-fork level switch | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 20 | [5 empty] | 3 |  | 自控阀门/仪表采购（316） / Procurement of control valves / instruments (316L) | 42 | 10月25 / 25 Oct | [52 empty] | 已订购 / Ordered
29 |  | 温度 / Temperature instrument | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 20 | [5 empty] | 4 |  | BPE管件采购（316） / Procurement of BPE fittings (316L) | 30 | 10月15 / 15 Oct | [52 empty] | 已订购 / Ordered
30 |  | PH / pH instrument | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 42 | [5 empty] | 5 |  | BPE手动阀门（316） / BPE manual valves (316L) | 30 | 10月15 / 15 Oct | [52 empty] | ——
31 |  | 压力 / Pressure instrument | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 21 | [5 empty] | 6 | 现场改造 / On-site modification | 管道、电气、彩板拆除 / Removal of piping, electrics and sandwich panels | 3 | [53 empty] | —— | bar: 12月 / December 8 to 12月 / December 11
32 |  | 手动隔膜阀 / Manual diaphragm valve | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 45 | [5 empty] | 7 |  | 钢平台拆除 / Removal of the steel platform | 2 | [53 empty] | —— | bar: 12月 / December 12 to 12月 / December 13
33 |  | BPE管道、管件 / BPE piping and fittings | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 35 | [5 empty] | 8 |  | 外墙拆除 / Removal of the external wall | 1 | bar: 12月 / December 14
制备系统-D级区-设备清单 / Preparation system – Grade D area – equipment list | [10 empty] | 安装周期 / Installation duration | 验证周期 / Qualification duration | 总计时间 / Total time | 技术要求 / Technical requirements |  | 9 |  | 设备拆除 / Equipment removal | 1 | bar: 12月 / December 15
序号 / No. | 设备位号 / Equipment tag | 设备名称 / Equipment name | 技术参数 / Technical parameters | 设备材质 / Equipment material | 使用介质 / Process medium | 单位 / Unit | 数量 / Quantity | 方案 / Option |  | 采购周期 / Procurement lead time | 40 | 验证18d（含空调验证），24h，不能受地面的影响 Qualification 18 d (including HVAC qualification), 24 h, must not be affected by the floor work 调试1d，空调EOQ+OQ5d，PQ12d，死时间 Commissioning 1 d, HVAC EOQ + OQ 5 d, PQ 12 d, dead time |  | 1、设备应满足ASME BPE要求，包括不限于如下要求： 1. The equipment shall comply with ASME BPE, including but not limited to: （1）设备接口采用NA接口，满足2D要求；接口尺寸及数量以确认图纸为准； (1) NA-type connections meeting the 2D drainability requirement; connection sizes and quantities as per the approved drawings; （2）设计淋洗口，需配淋洗球，满足全面清洗且通过核黄素清洗验证； (2) Spray port with spray ball, giving full coverage and passing the riboflavin coverage test; （3）出料口焊接隔膜阀，满足2D要求； (3) Diaphragm valve welded to the outlet, meeting the 2D requirement; （4）外表面抛光粗糙度<0.8um，内壁抛光粗糙度<0.4um； (4) External surface roughness < 0.8 µm, internal surface roughness < 0.4 µm; (5) 设备的原材、配件、生产制造及验收应严格按照ASME BPE要求进行，并提供相关证明资料； (5) Raw materials, components, manufacturing and acceptance strictly in line with ASME BPE, with the supporting documentation provided; 2、电机、减速机要求： 2. Motor and gearbox: （1）采用国内知名品牌；整体外包不锈钢，满足卫生级要求； (1) Well-known domestic brand; fully stainless-steel clad to sanitary standard; （2）防爆等级 ExdIIBT4 Gb，防护等级不低于IP55;电机能效不低于二级； (2) Explosion protection Ex d IIB T4 Gb, ingress protection not lower than IP55; motor efficiency class 2 or better; 3、机封采用双端面卫生级干磨机封，采用国内知名品牌； 3. Double-end sanitary dry-running mechanical seal from a well-known domestic brand; 4、搅拌材质与罐体一直，搅拌形式最终确认图纸为准； 4. Agitator material identical to the vessel; agitator design as per the approved drawings; 5、保温厚度满足温度要求，外壳采用3mm不锈钢，外表抛光粗糙度<0.8um， 5. Insulation thickness to suit the temperature requirement; cladding in 3 mm stainless steel with an external surface roughness < 0.8 µm, |  | 10 |  | 设备吊装、组装 / Equipment lifting and assembly | 2 | bar: 12月 / December 16 to 12月 / December 17
1 | 1211-HPPC03-AT03 | 组分接收搅拌罐（带夹套） / Fraction receiving agitated vessel (jacketed) | 1、有效容积8000L； 1. Working volume 8000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：316L不锈钢； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 购新安装 / Purchase new and install | 议价中，暂未确认供应商 / Under price negotiation; supplier not yet confirmed | 90 | [5 empty] | 11 |  | 钢平台恢复、外墙恢复 / Reinstatement of the steel platform and the external wall | 5 | bar: 12月 / December 18 to 12月 / December 22
2 | 1211-HPPC03-AT04/AT05 | 组分接收搅拌罐（带夹套） / Fraction receiving agitated vessel (jacketed) | 1、有效容积3000L； 1. Working volume 3000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：316L不锈钢； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂等 / Various organic solvents | 台 / unit | 2 | 购新安装 / Purchase new and install | 议价中，暂未确认供应商 / Under price negotiation; supplier not yet confirmed | 90 | [5 empty] | 12 |  | 彩钢板恢复 / Reinstatement of the sandwich panels | 5 | bar: 12月 / December 18 to 12月 / December 22
3 | 1211-HPPC03-AT06 | 样品搅拌罐（带夹套） / Sample agitated vessel (jacketed) | 1、有效容积1000L； 1. Working volume 1000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：316L不锈钢； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 购新安装 / Purchase new and install | 议价中，暂未确认供应商 / Under price negotiation; supplier not yet confirmed | 90 | [5 empty] | 13 |  | 设备管道安装 / Installation of equipment and piping | 10 | [53 empty] | 考虑提前预制部分管道 / Consider prefabricating part of the piping in advance | bar: 12月 / December 22 to 12月 / December 31
4 | 1211-HPPC03-T06 | 顶样搅拌罐（带夹套） / Top-fraction sample agitated vessel (jacketed) | 1、有效容积1000L； 1. Working volume 1000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：316L不锈钢； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 购新安装 / Purchase new and install | 议价中，暂未确认供应商 / Under price negotiation; supplier not yet confirmed | 90 |  |  |  | 设备应满足ASME BPE要求，包括不限于如下要求： The equipment shall comply with ASME BPE, including but not limited to: （1）设备接口采用NA接口，满足2D要求；接口尺寸及数量以确认图纸为准； (1) NA-type connections meeting the 2D drainability requirement; connection sizes and quantities as per the approved drawings; （2）设计淋洗口，需配淋洗球，满足全面清洗且通过核黄素清洗验证； (2) Spray port with spray ball, giving full coverage and passing the riboflavin coverage test; （3）出料口焊接隔膜阀，满足2D要求； (3) Diaphragm valve welded to the outlet, meeting the 2D requirement; （4）外表面抛光粗糙度<0.8um，内壁抛光粗糙度<0.4um； (4) External surface roughness < 0.8 µm, internal surface roughness < 0.4 µm; (5) 设备的原材、配件、生产制造及验收应严格按照ASME BPE要求进行，并提供相关证明资料； (5) Raw materials, components, manufacturing and acceptance strictly in line with ASME BPE, with the supporting documentation provided; |  | 14 |  | 电气、仪表安装 / Electrical and instrumentation installation | 5 | bar: 12月 / December 29 to 01月 / January 2
5 | *** | 组分接收储罐（不带夹套） / Fraction receiving storage tank (non-jacketed) | 有效容积100L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 100 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 12 | 购新安装 / Purchase new and install | 议价中，暂未确认供应商 / Under price negotiation; supplier not yet confirmed | 90 |  |  |  | 设备应满足ASME BPE要求，包括不限于如下要求： The equipment shall comply with ASME BPE, including but not limited to: （1）设备接口采用NA接口，满足2D要求，设备腔体可排净； (1) NA-type connections meeting the 2D drainability requirement, with a fully drainable equipment body; （2）外表面抛光粗糙度<0.8um，内壁抛光粗糙度<0.4um； (2) External surface roughness < 0.8 µm, internal surface roughness < 0.4 µm; （3）设备的原材、配件、生产制造及验收应严格按照ASME BPE要求进行，并提供相关证明资料； (3) Raw materials, components, manufacturing and acceptance strictly in line with ASME BPE, with the supporting documentation provided; |  | 15 |  | 地面施工、打胶处理 / Floor work and sealant treatment | 7 | bar: 01月 / January 3 to 01月 / January 9
| 1211-HPPC03-AT03-P01 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：12.5m3/h 扬程：25m 卡箍连接 变频 Rated flow 12.5 m³/h, head 25 m, clamp connection, variable speed | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2 | [6 empty] | 16 | 验证 / Qualification | 空调 / HVAC |  |  | 01月 / January 10: 涉及动火需要做一静一动5天培养 Hot work is involved, so one at-rest and one in-operation monitoring run with 5-day incubation is required
| 1211-HPPC03-AT03-P02 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：2m3/h 扬程：20m 卡箍连接 定频 Rated flow 2 m³/h, head 20 m, clamp connection, fixed speed | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2 | [6 empty] | 17 |  | 储罐、管路 / Storage tanks and piping | [54 empty] | 验证IQ与安装同步执行 / IQ runs in parallel with installation | bar: 01月 / January 11 to 01月 / January 15
| 1211-HPPC03-AT04-P01 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：12.5m3/h 扬程：25m 卡箍连接 变频 Rated flow 12.5 m³/h, head 25 m, clamp connection, variable speed | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2 | [6 empty] | 18 | 设备准别 / Equipment preparation | 清洗 / Cleaning | bar: 01月 / January 16 to 01月 / January 17
| 1211-HPPC03-AT05-P01 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：12.5m3/h 扬程：25m 卡箍连接 变频 Rated flow 12.5 m³/h, head 25 m, clamp connection, variable speed | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2
| 1211-HPPC03-AT06-P01 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：12.5m3/h 扬程：25m 卡箍连接 变频 Rated flow 12.5 m³/h, head 25 m, clamp connection, variable speed | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2
| 1211-HPPC03-T06-P01 | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：3.2m3/h 扬程：25m 卡箍连接 定频 Rated flow 3.2 m³/h, head 25 m, clamp connection, fixed speed | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2
6 | *** | 气动隔膜泵 / Pneumatic diaphragm pump | 5m³/h，25m，快开连接 / 5 m³/h, 25 m, quick-connect | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 2 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2
| *** | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：2m3/h 扬程：20m 卡箍连接 定频 Rated flow 2 m³/h, head 20 m, clamp connection, fixed speed | SS316L | 合格组分 / In-spec fractions | 台 / unit | 1 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2
| *** | 气动隔膜泵 / Pneumatic diaphragm pump | 额定流量：5m3/h 扬程：25m 卡箍连接 Rated flow 5 m³/h, head 25 m, clamp connection | SS316L | 不合格组分 / Out-of-spec fractions | 台 / unit | 1 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2
21 | 配件 / Components | 质量流量计（快开、BPE） / Mass flow meter (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 30
22 |  | 气动隔膜调节阀（快开、BPE） Pneumatic diaphragm control valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 42
23 |  | 气动隔膜开关阀（快开、BPE） Pneumatic diaphragm on/off valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 42
24 |  | 气动调节阀（快开、BPE） / Pneumatic control valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 42
25 |  | 气动开关阀（快开、BPE） / Pneumatic on/off valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 42
26 |  | 雷达液位计 / Radar level transmitter | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 20
27 |  | 音叉 / Tuning-fork level switch | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 20 | 安装周期 / Installation duration | 验证周期 / Qualification duration | 总计时间 / Total time | 技术要求 / Technical requirements
28 |  | 温度 / Temperature instrument | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 20 | 10 | 6d，24h 6 d, 24 h 验证IQ与安装同步执行，IQ在调试阶段关闭；调试1d，EOQ+OQ3d，PQ2d IQ runs in parallel with installation and is closed during commissioning; commissioning 1 d, EOQ + OQ 3 d, PQ 2 d |  | 设备应满足ASME BPE要求，包括不限于如下要求： The equipment shall comply with ASME BPE, including but not limited to: （1）设备接口采用NA接口，满足2D要求；接口尺寸及数量以确认图纸为准； (1) NA-type connections meeting the 2D drainability requirement; connection sizes and quantities as per the approved drawings; （2）设计淋洗口，需配淋洗球，满足全面清洗且通过核黄素清洗验证； (2) Spray port with spray ball, giving full coverage and passing the riboflavin coverage test; （3）出料口焊接隔膜阀，满足2D要求； (3) Diaphragm valve welded to the outlet, meeting the 2D requirement; （4）外表面抛光粗糙度<0.8um，内壁抛光粗糙度<0.4um； (4) External surface roughness < 0.8 µm, internal surface roughness < 0.4 µm; (5) 设备的原材、配件、生产制造及验收应严格按照ASME BPE要求进行，并提供相关证明资料； (5) Raw materials, components, manufacturing and acceptance strictly in line with ASME BPE, with the supporting documentation provided;
29 |  | PH / pH instrument | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 42 | [5 empty] | 超滤区改造-储罐及泵全部换新（316L）、改BPE管道（316L） Retrofit of the ultrafiltration area – replace all storage tanks and pumps with new units (316L) and convert to BPE piping (316L)
30 |  | 压力 / Pressure instrument | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 21 | [5 empty] | 序号 / No. | 工序 / Activity | 设备/材料 / Equipment / material | 货期/工期 / Lead time / duration | 预计到货时间 / Expected delivery date | 12月 / December 8: 12月 / December; 01月 / January 8: 01月 / January | 备注 / Remarks
31 |  | 手动隔膜阀 / Manual diaphragm valve | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 45 | [10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
32 |  | BPE管道、管件 / BPE piping and fittings | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 35 | [5 empty] | 1 | 设备采购 / Equipment procurement | 储罐到货（316） / Delivery of the storage tanks (316L) | 80 | 12月05 / 05 Dec | [52 empty] | 已订购 / Ordered | bar: 12月 / December 1 to 12月 / December 6
超滤系统设备清单 / Ultrafiltration system equipment list | [15 empty] | 2 |  | 自控阀门/仪表采购（316） / Procurement of control valves / instruments (316L) | 42 | 10月25 / 25 Oct | [52 empty] | 部分已订购、部分未订购，预估到货时间 Partly ordered, partly not ordered; estimated delivery date
序号 / No. | 设备位号 / Equipment tag | 设备名称 / Equipment name | 技术参数 / Technical parameters | 设备材质 / Equipment material | 使用介质 / Process medium | 单位 / Unit | 数量 / Quantity | 方案 / Option |  | 采购周期 / Procurement lead time | [5 empty] | 3 |  | BPE管件采购（316） / Procurement of BPE fittings (316L) | 30 | 10月15 / 15 Oct | [52 empty] | 已订购 / Ordered
1 | 1211-TFF01-T01 | 超滤接收储罐（带夹套） / Ultrafiltration receiving storage tank (jacketed) | 1、有效容积1000L； 1. Working volume 1000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 购新安装 / Purchase new and install | 议价中，暂未确认供应商 / Under price negotiation; supplier not yet confirmed | 75 | 安装周期 / Installation duration | 验证周期 / Qualification duration | 总计时间 / Total time | 技术要求 / Technical requirements |  | 4 |  | BPE手动阀门（316） / BPE manual valves (316L) | 30 | 10月15 / 15 Oct | [52 empty] | 已订购 / Ordered
2 | 配件 / Components | 质量流量计（快开、BPE） / Mass flow meter (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 30 | 30 | 18d（验证18d，）24h 18 d (qualification 18 d), 24 h 反应釜/三合一 Reactor / filter-dryer 需要重新验证 Requalification required 调试1d，空调EOQ+OQ5d，PQ12d，死时间 Commissioning 1 d, HVAC EOQ + OQ 5 d, PQ 12 d, dead time |  | 1、设备应满足ASME BPE要求，包括不限于如下要求： 1. The equipment shall comply with ASME BPE, including but not limited to: （1）设备接口采用NA接口，满足2D要求；接口尺寸及数量以确认图纸为准； (1) NA-type connections meeting the 2D drainability requirement; connection sizes and quantities as per the approved drawings; （2）设计淋洗口，需配淋洗球，满足全面清洗且通过核黄素清洗验证； (2) Spray port with spray ball, giving full coverage and passing the riboflavin coverage test; （3）出料口焊接隔膜阀，满足2D要求； (3) Diaphragm valve welded to the outlet, meeting the 2D requirement; （4）外表面抛光粗糙度<0.8um，内壁抛光粗糙度<0.4um； (4) External surface roughness < 0.8 µm, internal surface roughness < 0.4 µm; (5) 设备的原材、配件、生产制造及验收应严格按照ASME BPE要求进行，并提供相关证明资料； (5) Raw materials, components, manufacturing and acceptance strictly in line with ASME BPE, with the supporting documentation provided; 2、电机、减速机要求： 2. Motor and gearbox: （1）采用国内知名品牌；整体外包不锈钢，满足卫生级要求； (1) Well-known domestic brand; fully stainless-steel clad to sanitary standard; （2）防爆等级 ExdIIBT4 Gb，防护等级不低于IP55;电机能效不低于二级； (2) Explosion protection Ex d IIB T4 Gb, ingress protection not lower than IP55; motor efficiency class 2 or better; 3、机封采用双端面卫生级干磨机封，采用国内知名品牌； 3. Double-end sanitary dry-running mechanical seal from a well-known domestic brand; 4、搅拌材质与罐体一直，搅拌形式最终确认图纸为准； 4. Agitator material identical to the vessel; agitator design as per the approved drawings; 5、保温厚度满足温度要求，外壳采用3mm不锈钢，外表抛光粗糙度<0.8um， 5. Insulation thickness to suit the temperature requirement; cladding in 3 mm stainless steel with an external surface roughness < 0.8 µm, |  | 5 | 现场改造 / On-site modification | 彩钢板拆除、 / Removal of sandwich panels, | 1 | [53 empty] | 提前拆除 / Remove in advance | bar: 12月 / December 5
3 |  | 气动隔膜调节阀（快开、BPE） Pneumatic diaphragm control valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 42 | [5 empty] | 6 |  | 储罐拆、装 / Removal and installation of the storage tank | 1 | [53 empty] | —— | bar: 12月 / December 6
4 |  | 气动隔膜开关阀（快开、BPE） Pneumatic diaphragm on/off valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 42 | [5 empty] | 7 |  | BPE管道更换 / Replacement of BPE piping | 5 | [53 empty] | —— | bar: 12月 / December 5 to 12月 / December 9
5 |  | 手动隔膜阀 / Manual diaphragm valve | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 45 | [5 empty] | 8 |  | 电气、仪表安装 / Electrical and instrumentation installation | 3 | [53 empty] | —— | bar: 12月 / December 7 to 12月 / December 9
6 |  | BPE管道、管件 / BPE piping and fittings | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 35 |  |  |  | 1、设备应满足ASME BPE要求，包括不限于如下要求： 1. The equipment shall comply with ASME BPE, including but not limited to: （1）设备接口采用NA接口，满足2D要求；接口尺寸及数量以确认图纸为准； (1) NA-type connections meeting the 2D drainability requirement; connection sizes and quantities as per the approved drawings; （2）设计淋洗口，需配淋洗球，满足全面清洗且通过核黄素清洗验证； (2) Spray port with spray ball, giving full coverage and passing the riboflavin coverage test; （3）出料口焊接隔膜阀，满足2D要求； (3) Diaphragm valve welded to the outlet, meeting the 2D requirement; （4）外表面抛光粗糙度<0.8um，内壁抛光粗糙度<0.4um； (4) External surface roughness < 0.8 µm, internal surface roughness < 0.4 µm; (5) 设备的原材、配件、生产制造及验收应严格按照ASME BPE要求进行，并提供相关证明资料； (5) Raw materials, components, manufacturing and acceptance strictly in line with ASME BPE, with the supporting documentation provided; 2、电机、减速机要求： 2. Motor and gearbox: （1）采用国内知名品牌；整体外包不锈钢，满足卫生级要求； (1) Well-known domestic brand; fully stainless-steel clad to sanitary standard; （2）防爆等级 ExdIIBT4 Gb，防护等级不低于IP55;电机能效不低于二级； (2) Explosion protection Ex d IIB T4 Gb, ingress protection not lower than IP55; motor efficiency class 2 or better; 3、机封采用双端面卫生级干磨机封，采用进口知名品牌，如约翰克兰、伯格曼； 3. Double-end sanitary dry-running mechanical seal from a well-known imported brand such as John Crane or Burgmann; 4、搅拌材质与罐体一直，搅拌形式最终确认图纸为准； 4. Agitator material identical to the vessel; agitator design as per the approved drawings; 5、保温厚度满足温度要求，外壳采用3mm不锈钢，外表抛光粗糙度<0.8um， 5. Insulation thickness to suit the temperature requirement; cladding in 3 mm stainless steel with an external surface roughness < 0.8 µm, |  | 9 |  | 地面施工、打胶处理 / Floor work and sealant treatment | 5 | [53 empty] | 更换设备，考虑地面重做 / Equipment replacement; the floor is assumed to be redone | bar: 12月 / December 10 to 12月 / December 14
| *** | 气动隔膜泵 / Pneumatic diaphragm pump | 额定流量：5m3/h 扬程：25m 卡箍连接 Rated flow 5 m³/h, head 25 m, clamp connection | SS316L |  | 台 / unit | 1 |  | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | [6 empty] | 10 | 验证 / Qualification | 空调 / HVAC |  |  | 12月 / December 15: 涉及动火需要做一静一动5天培养 Hot work is involved, so one at-rest and one in-operation monitoring run with 5-day incubation is required
| TJ4S-1211-TFF02-WTK01-MP01 | 离心泵 / Centrifugal pump | 额定流量：3.2m3/h 扬程：20m Rated flow 3.2 m³/h, head 20 m | 304 |  | 台 / unit | 1 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2 | [6 empty] | 11 |  | 储罐、管路 / Storage tanks and piping | [54 empty] | 验证IQ与安装同步执行 / IQ runs in parallel with installation | bar: 12月 / December 16 to 12月 / December 20
| TJ4S-1211-TFF02-WTK01-MP02 | 离心泵 / Centrifugal pump | 额定流量：3.2m3/h 扬程：20m Rated flow 3.2 m³/h, head 20 m | 304 |  | 台 / unit | 1 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2 |  |  |  |  | 1、设备应满足ASME BPE要求，包括不限于如下要求： 1. The equipment shall comply with ASME BPE, including but not limited to: （1）外表面抛光粗糙度<0.8um，内壁抛光粗糙度<0.4um； (1) External surface roughness < 0.8 µm, internal surface roughness < 0.4 µm; (2) 设备的原材、配件、生产制造及验收应严格按照ASME BPE要求进行，并提供相关证明资料； (2) Raw materials, components, manufacturing and acceptance strictly in line with ASME BPE, with the supporting documentation provided; | 生产确认需求 / Requirement to be confirmed by Production | 12 | 设备准别 / Equipment preparation | 清洗 / Cleaning | bar: 12月 / December 21 to 12月 / December 22
沉淀釜区设备清单 / Precipitation reactor area equipment list
序号 / No. | 设备位号 / Equipment tag | 设备名称 / Equipment name | 技术参数 / Technical parameters | 设备材质 / Equipment material | 使用介质 / Process medium | 单位 / Unit | 数量 / Quantity | 方案 / Option |  | 采购周期 / Procurement lead time
1 | 1211-R01 | 析晶釜 / Crystallizer | 1、有效容积2000L； 1. Working volume 2000 L; 2、釜内设计温度-25~200℃，夹套设计温度-25~220℃； 2. Reactor design temperature −25 to 200 °C, jacket design temperature −25 to 220 °C; 3、釜内设计压力-0.1~0.4MPa；夹套工作压力0.6Mpa； 3. Reactor design pressure −0.1 to 0.4 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：304不锈钢衬C22或C276； Product contact: 304 stainless steel lined with C22 or C276; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、酸、碱等 / Various organic solvents, acids, bases, etc. | 台 / unit | 1 | 购新安装 / Purchase new and install | 议价中，暂未确认供应商 / Under price negotiation; supplier not yet confirmed | 100
3 | 1211-AT01 | 搅拌罐 / Agitated vessel | 1、有效容积600L； 1. Working volume 600 L; 2、罐内设计温度-25~200℃，夹套设计温度-25~220℃； 2. Vessel design temperature −25 to 200 °C, jacket design temperature −25 to 220 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：316L不锈钢； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、盐溶液等 / Various organic solvents, salt solutions, etc. | 台 / unit | 1 | 购新安装 / Purchase new and install | 议价中，暂未确认供应商 / Under price negotiation; supplier not yet confirmed | 75
4 | 1211-AT02 | 搅拌罐 / Agitated vessel | 1、有效容积80L； 1. Working volume 80 L; 2、罐内设计温度-25~200℃，夹套设计温度-25~220℃； 2. Vessel design temperature −25 to 200 °C, jacket design temperature −25 to 220 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：316L不锈钢； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、酸、碱等 / Various organic solvents, acids, bases, etc. | 台 / unit | 1 | 购新安装 / Purchase new and install | 议价中，暂未确认供应商 / Under price negotiation; supplier not yet confirmed | 75
| TJ4S-1211-AT02-P02 | 气动隔膜泵 / Pneumatic diaphragm pump | 额定流量：5m3/h 扬程：25m 卡箍连接 Rated flow 5 m³/h, head 25 m, clamp connection | SS316L |  | 台 / unit | 1 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2
15 | TJ4S-1211-AT01-P01 | 卫生级四元隔膜泵 / Sanitary four-head diaphragm pump | 额定流量：200L/h BPE接口 卡箍连接 Rated flow 200 L/h, BPE connection, clamp connection | 316L | 浓盐溶液 / Concentrated salt solution | 台 / unit | 1 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2
16 | TJ4S-1211-AT02-P01 | 卫生级四元隔膜泵 / Sanitary four-head diaphragm pump | 额定流量：20L/h BPE接口 卡箍连接 Rated flow 20 L/h, BPE connection, clamp connection | 316L | 浓盐溶液 / Concentrated salt solution | 台 / unit | 1 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2
5 | 1211-Fd01 | 三合一 / Filter-dryer | 1、设备尺寸DN1200； 1. Equipment size DN1200; 2、罐内设计温度-25~200℃，夹套设计温度-25~220℃； 2. Vessel design temperature −25 to 200 °C, jacket design temperature −25 to 220 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：304不锈钢衬C22或C276； Product contact: 304 stainless steel lined with C22 or C276; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、酸、碱等 / Various organic solvents, acids, bases, etc. | 台 / unit | 1 | 购新安装 / Purchase new and install | 议价中，暂未确认供应商 / Under price negotiation; supplier not yet confirmed | 120
7 | *** | 旋分筛 / Rotary sifter | 处理量200kg/h. Throughput 200 kg/h. | SS316L | 固体 / Solids | 台 / unit | 1 | 购新安装 / Purchase new and install | 使用方案1、方案2设备，均是新采购 Use the equipment from Option 1 / Option 2; all newly purchased | ？
8 | 配件 / Components | 质量流量计（快开、BPE） / Mass flow meter (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 30
9 |  | 气动隔膜调节阀（快开、BPE） Pneumatic diaphragm control valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 42
10 |  | 气动隔膜开关阀（快开、BPE） Pneumatic diaphragm on/off valve (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 42 | [5 empty] | 沉淀区改造-沉淀釜、三合一（HC）、600L储罐、80L储罐全部换新、改BPE管道（316L） Retrofit of the precipitation area – replace the precipitation reactor, filter-dryer (Hastelloy), 600 L storage tank and 80 L storage tank with new units and convert to BPE piping (316L)
11 |  | 手动隔膜阀 / Manual diaphragm valve | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 45 | [5 empty] | 序号 / No. | 工序 / Activity | 设备/材料 / Equipment / material | 货期/工期 / Lead time / duration | 预计到货时间 / Expected delivery date | 12月 / December 1: 12月 / December; 12月 / December 18: 01月 / January; 01月 / January 18: 2月 / February
12 |  | BPE管道、管件 / BPE piping and fittings | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 新采购 / Newly purchased | 使用方案1、方案2配件 / Use the components from Option 1 / Option 2 | 35
| TJ4S-1211-FD01-Tr01-P01 | 气动隔膜泵 / Pneumatic diaphragm pump | 额定流量：5m3/h 扬程：30m 卡箍连接 Rated flow 5 m³/h, head 30 m, clamp connection | 防腐 / Corrosion-resistant |  | 台 / unit | 1 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2
| TJ4S-1211-FD01-Tr01-P02 | 气动隔膜泵 / Pneumatic diaphragm pump | 额定流量：5m3/h 扬程：30m 卡箍连接 Rated flow 5 m³/h, head 30 m, clamp connection | 防腐 / Corrosion-resistant |  | 台 / unit | 1 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2
| TJ4S-1212-FD06-Tr01-P01 | 气动隔膜泵 / Pneumatic diaphragm pump | 额定流量：5m3/h 扬程：30m 卡箍连接 Rated flow 5 m³/h, head 30 m, clamp connection | 防腐 / Corrosion-resistant |  | 台 / unit | 1 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2 | [11 empty] | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 1 | 2 | 3 | 4 | 备注 / Remarks
| *** | 卫生级离心泵 / Sanitary centrifugal pump | 额定流量：2m3/h 扬程：20m 卡箍连接 定频 Rated flow 2 m³/h, head 20 m, clamp connection, fixed speed | SS316L | 注射水 / Water for injection | 台 / unit | 2 |  | 使用方案1、方案2泵 / Use the pumps from Option 1 / Option 2 | [6 empty] | 1 | 设备采购 / Equipment procurement | 2000LHC釜到货 / Delivery of the 2000 L Hastelloy reactor | 100 | 12月25 / 25 Dec | [52 empty] | 已订购 / Ordered | bar: 15 to 23
[16 empty] | 2 |  | DN1200三合一到货 / Delivery of the DN1200 filter-dryer | 100 | 12月25 / 25 Dec | [52 empty] | 已订购 / Ordered | bar: 15 to 23
[16 empty] | 3 |  | 储罐到货（316） / Delivery of the storage tanks (316L) | 90 | 12月15 / 15 Dec | [52 empty] | 未订购，预估到货时间 / Not ordered yet, estimated delivery date | bar: 15
[16 empty] | 4 |  | 离心泵到货（316） / Delivery of the centrifugal pumps (316L) | 42 | 10月25 / 25 Oct | [52 empty] | 未订购，预估到货时间 / Not ordered yet, estimated delivery date
[16 empty] | 5 |  | 自控阀门/仪表采购（316） / Procurement of control valves / instruments (316L) | 42 | 10月25 / 25 Oct | [52 empty] | 部分已订购、部分未订购，预估到货时间 Partly ordered, partly not ordered; estimated delivery date
[16 empty] | 6 |  | BPE管件采购（316） / Procurement of BPE fittings (316L) | 30 | 10月15 / 15 Oct | [52 empty] | 已订购 / Ordered
[16 empty] | 7 |  | BPE手动阀门（316） / BPE manual valves (316L) | 30 | 10月15 / 15 Oct | [52 empty] | 已订购 / Ordered
[16 empty] | 8 |  | BPE管件（HC） / BPE fittings (Hastelloy) | 60 | 11月30 / 30 Nov | [52 empty] | 已订购 / Ordered
[16 empty] | 9 | 现场改造 / On-site modification | 管道、电气、彩板拆除 / Removal of piping, electrics and sandwich panels | 4 | [53 empty] | 设备到货前提前1周拆除 / Remove one week before the equipment arrives | bar: 15 to 18
[16 empty] | 10 |  | 钢平台拆除 / Removal of the steel platform | 2 | bar: 19 to 20
[16 empty] | 11 |  | 外墙拆除 / Removal of the external wall | 1 | bar: 21
[16 empty] | 12 |  | 设备拆除 / Equipment removal | 1 | bar: 22
[16 empty] | 13 |  | 设备吊装、组装 / Equipment lifting and assembly | 2 | [53 empty] | —— | bar: 23 to 24
[16 empty] | 14 |  | 钢平台恢复、外墙恢复 / Reinstatement of the steel platform and the external wall | 5 | [53 empty] | —— | bar: 25 to 29
[16 empty] | 15 |  | 彩钢板恢复 / Reinstatement of the sandwich panels | 5 | [53 empty] | —— | bar: 25 to 29
[16 empty] | 16 |  | 设备管道安装 / Installation of equipment and piping | 10 | [53 empty] | —— | bar: 28 to 6
[16 empty] | 17 |  | 电气、仪表安装 / Electrical and instrumentation installation | 5 | [53 empty] | —— | bar: 3 to 7
[16 empty] | 18 |  | 地面施工、打胶处理 / Floor work and sealant treatment | 7 | [53 empty] | 破坏面积大，需要重新做地面，细节处理等 Large damaged area; the floor has to be redone, including detail work | bar: 8 to 14
[16 empty] | 19 | 验证 / Qualification | 空调 / HVAC |  |  | 15: 涉及动火需要做一静一动5天培养 Hot work is involved, so one at-rest and one in-operation monitoring run with 5-day incubation is required
[16 empty] | 20 |  | 储罐、管路 / Storage tanks and piping | bar: 16 to 20
[16 empty] | 21 | 设备准别 / Equipment preparation | 清洗 / Cleaning | bar: 21 to 22

## 客户整改问题评估 Findings
[16 empty] | 9月 / September | [13 empty] | 10月 / October | [30 empty] | 11月 / November
序号 / No. |  | 设备位号 / Equipment tag | 设备名称 / Equipment name | 技术参数 / Technical parameters | 设备材质 / Equipment material | 使用介质 / Process medium | 单位 / Unit | 数量 / Quantity | 部件 / Component | 内部评估详情--改造方案 / Internal assessment – rectification plan | 目前进展 / Current status | 采购时间 / Procurement time | 安装周期 / Installation duration | 验证清洗 / Qualification and cleaning | 总计时间 / Total time | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | 制备配液 / Preparation / solution preparation | 1213-R05 | 哈氏合金反应釜 / Hastelloy reactor | 3000L哈氏合金釜 / 3000 L Hastelloy reactor | C276 | 浓盐溶液 / Concentrated salt solution | 台 / unit | 1 | 设备本体 / Equipment body | 1.搅拌：螺母固定-更改一体式搅拌桨 1. Agitator: nut-fixed blades – change to a one-piece impeller 2.上口： 2. Top nozzles: 2.1管口全部法兰连接，需要更换为压力表/视镜为N/A口；物料、氮气、尾气为快开口 2.1 All nozzles are flanged; the pressure gauge and sight glass have to be changed to NA-type nozzles; material, nitrogen and off-gas nozzles to quick-connect 2.2无内伸管-液面上滴加-盐酸滴加：-需要增加 2.2 No dip tube – dosing above the liquid level – hydrochloric acid dosing: to be added 2.3无PH计在线检测-需要增加 2.3 No in-line pH measurement – to be added 2.4无在线取样口-需要增加； 2.4 No in-line sampling port – to be added 2.5固体投料目前球阀-需要更换为蝶阀；投料方式-密闭投料； 2.5 Solids charging currently through a ball valve – to be changed to a butterfly valve; charging method: closed charging 2.6温度计口-温度计套管类型讨论-密闭套管 2.6 Thermometer nozzle – thermowell type under discussion – closed thermowell 3.下口： 3. Bottom nozzle: 3.1罐底口隔膜阀 3.1 Diaphragm valve at the vessel bottom outlet 4.侧口： N/A 4. Side nozzles: N/A | 1、方案确定，IEPE绘图中，物资工程确认货期，T型阀6-7周，改造3天。 1. Concept fixed, IEPE is preparing the drawings, Materials / Engineering is confirming lead times, T-valves 6–7 weeks, modification 3 days. | 40天 / 40 days | 10天 / 10 days | 4d（钝化1天+验证2d+清洗1d） 4 d (passivation 1 d + qualification 2 d + cleaning 1 d)
2 | [8 empty] | 管路 / Piping | 1.氮气：评估无异常，客户现场提出； 1. Nitrogen: assessment shows no issue; raised by the customer on site 2.尾气：评估无异常，客户现场提出； 2. Off-gas: assessment shows no issue; raised by the customer on site 3.溶剂管线: 未提出问题 3. Solvent lines: no issue raised 4. 物料管线: 4. Material lines: 釜上口管线：4.1罐区溶剂管路-未提出疑问； Reactor top lines: 4.1 Solvent lines in the tank farm – no question raised 4.2 139788-step3A-P01 纯化管路-设计不合理（阀门2D、坡度、氮气吹扫、末端取样、末端冲洗排放、定量加料顺序控制-SOP）：整改按照标准示意图进行更改 4.2 139788-step3A-P01 purification line – design not suitable (valve 2D, slope, nitrogen purge, end-of-line sampling, end-of-line flush and drain, metered charging sequence control – SOP): rectified according to the standard reference diagram 釜下口管线：（需要专家评估，或者同客户深入讨论排尽点） Reactor bottom lines: (expert assessment or a detailed discussion of the drain points with the customer is needed) 4.3、139788-step3A-P01：R05下口至1211-HPPC03-AT01/AT02管线 4.3 139788-step3A-P01: line from the R05 bottom outlet to 1211-HPPC03-AT01 / AT02 1.过滤器前后增加低点排净； 1. Add low-point drains upstream and downstream of the filter 2.去两台设备分支管路：两个阀门2D需求； 2. Branch lines to the two units: 2D requirement for both valves 4.4、139788-step3A-P03：R05下口至1211-HPPC03-AT01管线 4.4 139788-step3A-P03: line from the R05 bottom outlet to 1211-HPPC03-AT01 1.物料设备根部-增加排净点：管路冲洗；（需要专家评估，或者同客户深入讨论排尽点） 1. Add a drain point at the root of the equipment: line flushing (expert assessment or a detailed discussion of the drain points with the customer is needed) 4.5、139788-step3A-P02：R05下口至1211-HPPC03-AT02管线 4.5 139788-step3A-P02: line from the R05 bottom outlet to 1211-HPPC03-AT02 1.未提出需求 1. No requirement raised | 1、方案确定，IEPE绘图中，物资工程确认货期，T型阀预算已提报，货期6-7周，改造5天。 1. Concept fixed, IEPE is preparing the drawings, Materials / Engineering is confirming lead times, the T-valve budget has been submitted, lead time 6–7 weeks, modification 5 days. 2、纯水排水进行重新设计，需要保证使用前润洗，排空，以及使用后的吹干。其他排水管路需要同步进行考虑。 2. The purified-water drain is being redesigned; pre-use rinsing and draining and post-use blow-drying have to be ensured. The other drain lines have to be considered at the same time. 3、增加盐酸加料管路提前的准备制作。 3. Prepare and prefabricate the additional hydrochloric acid charging line in advance. | 49天 / 49 days | 5天 / 5 days
3 | [8 empty] | 仪表 / Instruments | 1.压力： 1. Pressure: 保证2D，直接安装至管口，取消手阀；-需要整改 mount directly on the nozzle to keep 2D and delete the hand valve – rectification needed 2.温度： 2. Temperature: 内伸管-保证密闭-禁止螺纹密封形式-整改 dip tube – must be closed – threaded sealing not allowed – rectification 3.pH计 3. pH: ：无侧口（检测）-循环取样-PH检测； no side nozzle (measurement) – pH measured on a recirculation sample 4.液位计：差压/雷达/音叉：目前没有配置； 4. Level: differential pressure / radar / tuning fork – none currently installed 5.质量流量计：安装方向-调整为横向安装； 5. Mass flow meter: mounting orientation – change to horizontal installation | 温度、压力已提报预算采购 / The temperature and pressure instruments have been submitted for budget and purchase | 30天 / 30 days | 1天 / 1 day
4 | [8 empty] | 泵 / Pumps | 无配置 / Not installed
5 | [8 empty] | 阀门 / Valves | 氮气\尾气根部阀门:之前球阀,需要更换为哈氏合金隔膜阀或盲板; Root valves of the nitrogen / off-gas lines: currently ball valves, to be replaced by Hastelloy diaphragm valves or blinds; 其他阀门整体更换哈氏合金隔膜阀或盲板; all other valves to be replaced by Hastelloy diaphragm valves or blinds | 隔膜阀预算已经提报，316L与哈氏合金隔膜阀同步采购 The diaphragm valve budget has been submitted; the 316L and Hastelloy diaphragm valves are purchased together | 40天 40 days 70天 70 days
6 |  | 1211-HPPC03-AT01 | 配液搅拌罐（不带夹套） / Solution preparation agitated vessel (non-jacketed) | 有效容积500L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 500 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | C276 | 浓盐溶液 / Concentrated salt solution | 台 / unit | 1 | 设备本体 / Equipment body | 储罐整体更换英德316L 600L储罐； The tank is completely replaced by a Yingde 316L 600 L storage tank; 1.搅拌：一体式搅拌桨 1. Agitator: one-piece impeller 2.上口：管口不满足2D需求-需要更换储罐； 2. Top nozzles: the nozzles do not meet the 2D requirement – the tank has to be replaced; 3.下口：评估无异常，客户现场提出； 3. Bottom nozzle: assessment shows no issue; raised by the customer on site 4.侧口： 评估无异常，客户现场提出； 4. Side nozzles: assessment shows no issue; raised by the customer on site | 已经订货 / Ordered | 30天+20天 / 30 days + 20 days | 21天 / 21 days | 1d
7 | [8 empty] | 管路 / Piping | 1.氮气：根部球阀-需要更换为隔膜阀； 1. Nitrogen: root ball valve – to be replaced by a diaphragm valve; 2.尾气：根部球阀-需要更换为隔膜阀； 2. Off-gas: root ball valve – to be replaced by a diaphragm valve; 3.溶剂：不涉及 3. Solvent: not applicable 4.物料: 4. Material: 4.1:1211-HPPC03-AT01-P01 纯化管路 4.1 1211-HPPC03-AT01-P01 purification line 设计不合理（阀门2D、坡度、氮气吹扫、末端取样、末端冲洗排放、定量加料顺序控制-SOP）：整改按照标准示意图进行更改; design not suitable (valve 2D, slope, nitrogen purge, end-of-line sampling, end-of-line flush and drain, metered charging sequence control – SOP): rectified according to the standard reference diagram; 4.2 139788-step3A-P03 R05反应釜至1211-HPPC03-AT01管道 4.2 139788-step3A-P03 line from reactor R05 to 1211-HPPC03-AT01 物料管线阀门，按照BPE管路更换； material line valves to be replaced to BPE piping standard; 4.3 1211-HPPC03-AT01-P02: AT01下口至1211-HPPC03-AT01-P01入口管道 4.3 1211-HPPC03-AT01-P02: line from the AT01 bottom outlet to the inlet of 1211-HPPC03-AT01-P01 按照BPE管路制作-管路低点排净; built to BPE piping standard – low-point drain in the line; 4.4 1211-HPPC03-T03-P01: 1211-HPPC03-AT01-P01至T03管道 4.4 1211-HPPC03-T03-P01: line from 1211-HPPC03-AT01-P01 to T03 静态混合\PH计\电导率仪安装需要按照BPE需求整改,扩管需要增加排净点; the static mixer, pH meter and conductivity meter installations have to be rectified to BPE requirements; a drain point has to be added at the pipe enlargement; 三通开关阀XV-HPPC03-T03-01:排废至废液管路需要增加止回阀; Three-way on/off valve XV-HPPC03-T03-01: a check valve has to be added on the waste discharge line to the waste header | BPE管路、隔膜阀已采购，已下单，预计10月中开始施工 The BPE piping and diaphragm valves are purchased and ordered; construction is expected to start in mid-October | 28天 / 28 days | 21天 / 21 days
8 | [8 empty] | 仪表 / Instruments | 1.压力： 1. Pressure: 取消根部阀-保证2D安装 delete the root valve – keep a 2D installation 2.温度： 2. Temperature: 不涉及 not applicable 3.pH计 3. pH: : 不涉及 not applicable 4.差压/雷达/音叉：差压不满2D需求，需要改为雷达与音叉 4. Differential pressure / radar / tuning fork: differential pressure does not meet the 2D requirement and has to be changed to radar and tuning fork | 压力、音叉、雷达预算已提报，未定供应商 The pressure, tuning-fork and radar instruments have been submitted for budget; supplier not yet selected | 30天 / 30 days | 2天 / 2 days
9 | [8 empty] | 泵 / Pumps | 柱塞计量:1211-HPPC03-AT01-P01 Plunger metering pump: 1211-HPPC03-AT01-P01 泵入口及泵出口保留低点排净:- 评估无异常，客户现场提出； Keep the low-point drains at the pump inlet and outlet: assessment shows no issue; raised by the customer on site | 四元隔膜泵-同步采购中 / Four-head diaphragm pumps – being purchased in parallel
10 | [8 empty] | 阀门 / Valves | 管路含有球阀需要更换为隔膜阀; The line contains ball valves that have to be replaced by diaphragm valves | 316L隔膜阀已采购，预计10月20号到货 The 316L diaphragm valves are purchased and are expected on 20 October | 28天 / 28 days | 21天 / 21 days
11 |  | 1211-HPPC03-AT02 | 配液搅拌罐（不带夹套） / Solution preparation agitated vessel (non-jacketed) | 有效容积300L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 300 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | C276 | 浓盐溶液 / Concentrated salt solution | 台 / unit | 1 | 设备本体 / Equipment body | 储罐整体更换英德316L 600L储罐；(300L HC储罐返厂改造快开口) The tank is completely replaced by a Yingde 316L 600 L storage tank; (the 300 L Hastelloy tank goes back to the factory to be converted to quick-connect nozzles) 1.搅拌：一体式搅拌桨 1. Agitator: one-piece impeller 2.上口：管口不满足2D需求-需要更换储罐； 2. Top nozzles: the nozzles do not meet the 2D requirement – the tank has to be replaced; 3.下口：评估无异常，客户现场提出； 3. Bottom nozzle: assessment shows no issue; raised by the customer on site 4.侧口： 评估无异常，客户现场提出； 4. Side nozzles: assessment shows no issue; raised by the customer on site | 待上报预算；哈氏合金罐返厂改造25天 Budget still to be submitted; return-to-factory modification of the Hastelloy tank takes 25 days | 30天+20天 / 30 days + 20 days | 21天 / 21 days | 1d
12 | [8 empty] | 管路 / Piping | 1.氮气：根部球阀-需要更换为隔膜阀； 1. Nitrogen: root ball valve – to be replaced by a diaphragm valve; 2.尾气：根部球阀-需要更换为隔膜阀； 2. Off-gas: root ball valve – to be replaced by a diaphragm valve; 3.溶剂：不涉及 3. Solvent: not applicable 4.物料： 4. Material: 4.1 1211-HPPC03-AT02-P01 纯化水管路 4.1 1211-HPPC03-AT02-P01 purified-water line 设计不合理（阀门2D、坡度、氮气吹扫、末端取样、末端冲洗排放、定量加料顺序控制-SOP）：整改按照标准示意图进行更改 design not suitable (valve 2D, slope, nitrogen purge, end-of-line sampling, end-of-line flush and drain, metered charging sequence control – SOP): rectified according to the standard reference diagram 4.2 139788-step3A-P02 R05-P01至1211-HPPC03-AT02管道 4.2 139788-step3A-P02 line from R05-P01 to 1211-HPPC03-AT02 按照BPE管路制作-管路低点排净\仪表阀门满足2D要求,球阀更换为隔膜阀 built to BPE piping standard – low-point drain in the line; instrument valves meeting the 2D requirement; ball valves replaced by diaphragm valves 4.3 AT02下口至1211-HPPC03-AT02-P01入口管线 4.3 Line from the AT02 bottom outlet to the inlet of 1211-HPPC03-AT02-P01 按照BPE管路制作-管路低点排净\仪表阀门满足2D要求,球阀更换为隔膜阀 built to BPE piping standard – low-point drain in the line; instrument valves meeting the 2D requirement; ball valves replaced by diaphragm valves | BPE管路、隔膜阀已采购，已下单，预计10月中开始施工 The BPE piping and diaphragm valves are purchased and ordered; construction is expected to start in mid-October | 28天 / 28 days | 21天 / 21 days
13 | [8 empty] | 仪表 / Instruments | 1.压力： 1. Pressure: 取消根部阀-保证2D安装 delete the root valve – keep a 2D installation 2.温度： 2. Temperature: 不涉及 not applicable 3.pH计 3. pH: : 不涉及 not applicable 4.差压/雷达/音叉：差压不满2D需求，需要改为雷达与音叉 4. Differential pressure / radar / tuning fork: differential pressure does not meet the 2D requirement and has to be changed to radar and tuning fork | 压力、音叉、雷达预算已提报，未定供应商 The pressure, tuning-fork and radar instruments have been submitted for budget; supplier not yet selected | 30天 / 30 days | 2天 / 2 days
14 | [8 empty] | 泵 / Pumps | 柱塞计量:1211-HPPC03-AT01-P02 Plunger metering pump: 1211-HPPC03-AT01-P02 泵入口及泵出口保留低点排净:- 评估无异常，客户现场提出； Keep the low-point drains at the pump inlet and outlet: assessment shows no issue; raised by the customer on site | 四元隔膜泵-同步采购中 / Four-head diaphragm pumps – being purchased in parallel
15 | [8 empty] | 阀门 / Valves | 管路含有球阀需要更换为隔膜阀; The line contains ball valves that have to be replaced by diaphragm valves | 316L隔膜阀已采购，预计10月20号到货 The 316L diaphragm valves are purchased and are expected on 20 October | 28天 / 28 days | 21天 / 21 days
16 |  | 1211-HPPC03-T01 | 纯水储罐（不带夹套） / Purified water storage tank (non-jacketed) | 有效容积1000L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 1000 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 纯化水 / Purified water | 台 / unit | 1 | 设备本体 / Equipment body | 储罐整体更换英德316L 1500L储罐； The tank is completely replaced by a Yingde 316L 1500 L storage tank; 1.搅拌：不涉及 1. Agitator: not applicable 2.上口：罐口不满足2D： 2. Top nozzles: nozzles do not meet 2D: 3.下口：罐口不满足2D： 3. Bottom nozzle: nozzle does not meet 2D: 4.侧口：罐口不满足2D： 4. Side nozzles: nozzles do not meet 2D: | 更换英德储罐，储罐预算达总审批中。 Replace with a Yingde tank; the tank budget is under final approval. | 30+20 |  | 5d（验证4d+清洗1d） / 5 d (qualification 4 d + cleaning 1 d)
17 | [8 empty] | 管路 / Piping | 1.氮气：不涉及 1. Nitrogen: not applicable 2.尾气：根部球阀-需要更换为隔膜阀； 2. Off-gas: root ball valve – to be replaced by a diaphragm valve; 3.溶剂：不涉及 3. Solvent: not applicable 4.物料： 4. Material: 4.1 1211-HPPC03-T01-P01纯化水管路 4.1 1211-HPPC03-T01-P01 purified-water line 设计不合理（阀门2D、坡度、氮气吹扫、末端取样、末端冲洗排放、定量加料顺序控制-SOP）：整改按照标准示意图进行更改 design not suitable (valve 2D, slope, nitrogen purge, end-of-line sampling, end-of-line flush and drain, metered charging sequence control – SOP): rectified according to the standard reference diagram 4.2 1211-HPPC03-T01-P02 泵1211-HPPC03-T03-P01出口至1211-HPPC03-T01储罐管线 4.2 1211-HPPC03-T01-P02 line from the outlet of pump 1211-HPPC03-T03-P01 to storage tank 1211-HPPC03-T01 需要按照BPE管路更改，死角，排净;（做死角评估） has to be changed to BPE piping; dead legs and drainability (dead-leg assessment to be carried out) 4.3 T01储罐下口至泵1211-HPPC03-T01-P01入口管线 4.3 Line from the T01 tank bottom outlet to the inlet of pump 1211-HPPC03-T01-P01 需要按照BPE管路更改，死角，排净;（做死角评估） has to be changed to BPE piping; dead legs and drainability (dead-leg assessment to be carried out) 4.4 1211-HPPC03-T01-P04 T01储罐下口至泵1211-HPPC03-T01-P02入口管线 4.4 1211-HPPC03-T01-P04 line from the T01 tank bottom outlet to the inlet of pump 1211-HPPC03-T01-P02 需要按照BPE管路更改，死角，排净;（做死角评估） has to be changed to BPE piping; dead legs and drainability (dead-leg assessment to be carried out) 4.5 1211-HPPC03-T01-P05 T01储罐下口至泵1211-HPPC03-T03-P01和泵1318-HPPC03-T03-P02入口管线 4.5 1211-HPPC03-T01-P05 line from the T01 tank bottom outlet to the inlets of pumps 1211-HPPC03-T03-P01 and 1318-HPPC03-T03-P02 需要按照BPE管路更改，死角，排净;（做死角评估） has to be changed to BPE piping; dead legs and drainability (dead-leg assessment to be carried out) | 1、罐上口阀门需核实尺寸数量 1. The size and quantity of the valves on the tank top have to be verified 2、BPE管路已采购，预计10月20号到货 2. The BPE piping is purchased and is expected on 20 October | 28天 / 28 days | 21天 / 21 days
18 | [8 empty] | 仪表 / Instruments | 1.压力： 1. Pressure: 取消根部阀-保证2D安装 delete the root valve – keep a 2D installation 2.温度： 2. Temperature: 不涉及 not applicable 3.pH计 3. pH: : 不涉及 not applicable 4.差压/雷达/音叉：差压液位不满足2D需求取消，雷达液位计按照满足2D，增加音叉 4. Differential pressure / radar / tuning fork: the differential-pressure level measurement does not meet 2D and is deleted; the radar level transmitter is installed to meet 2D and a tuning fork is added | 压力、音叉、雷达预算已提报，未定供应商 The pressure, tuning-fork and radar instruments have been submitted for budget; supplier not yet selected | 30天 / 30 days | 2天 / 2 days
19 | [8 empty] | 泵 / Pumps | 柱塞计量:1211-HPPC03-T01-P01/1211-HPPC03-T01-P02 Plunger metering pumps: 1211-HPPC03-T01-P01 / 1211-HPPC03-T01-P02 泵入口及泵出口保留低点排净:- 评估无异常，客户现场提出； Keep the low-point drains at the pump inlet and outlet: assessment shows no issue; raised by the customer on site | 四元隔膜泵-同步采购中 / Four-head diaphragm pumps – being purchased in parallel
20 | [8 empty] | 阀门 / Valves | 管路含有球阀需要更换为隔膜阀; The line contains ball valves that have to be replaced by diaphragm valves | 316L隔膜阀已采购，预计10月20号到货 The 316L diaphragm valves are purchased and are expected on 20 October | 28天 / 28 days | 21天 / 21 days
21 |  | 1211-HPPC03-T02 | 乙腈储罐（不带夹套） / Acetonitrile storage tank (non-jacketed) | 有效容积1000L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 1000 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 新鲜乙腈、备用 / Fresh acetonitrile, spare | 台 / unit | 1 | 设备本体 / Equipment body | 1.搅拌：不涉及 1. Agitator: not applicable 2.上口：评估无异常，客户现场提出； 2. Top nozzles: assessment shows no issue; raised by the customer on site 3.下口：评估无异常，客户现场提出； 3. Bottom nozzle: assessment shows no issue; raised by the customer on site 4.侧口：评估无异常，客户现场提出； 4. Side nozzles: assessment shows no issue; raised by the customer on site | N/A | 30+20 |  | 5d（验证4d+清洗1d） / 5 d (qualification 4 d + cleaning 1 d)
22 | [8 empty] | 管路 / Piping | 1.氮气：评估无异常，客户现场提出； 1. Nitrogen: assessment shows no issue; raised by the customer on site 2.尾气：评估无异常，客户现场提出； 2. Off-gas: assessment shows no issue; raised by the customer on site 3.溶剂： 3. Solvent: 3.1 新鲜乙腈进料管线 3.1 Fresh acetonitrile charging line 4.物料---评估无异常，客户现场提出； 4. Material – assessment shows no issue; raised by the customer on site 4.1 1211-HPPC03-T02-P01 泵1211-HPPC03-T04-P01出口至1211-HPPC03-T02乙腈储罐管线 4.1 1211-HPPC03-T02-P01 line from the outlet of pump 1211-HPPC03-T04-P01 to acetonitrile storage tank 1211-HPPC03-T02 4.2 T02储罐下口至泵1211-HPPC03-T02-P01入口管线 4.2 Line from the T02 tank bottom outlet to the inlet of pump 1211-HPPC03-T02-P01 4.3 T02储罐下口至泵1211-HPPC03-T02-P02入口管线 4.3 Line from the T02 tank bottom outlet to the inlet of pump 1211-HPPC03-T02-P02 4.3 1211-HPPC03-T02-P04 T02储罐下口至泵1211-HPPC03-T04-P01入口管线 4.3 1211-HPPC03-T02-P04 line from the T02 tank bottom outlet to the inlet of pump 1211-HPPC03-T04-P01 | 1、罐上口阀门需核实尺寸数量 1. The size and quantity of the valves on the tank top have to be verified 2、BPE管路已采购，预计10月20号到货 2. The BPE piping is purchased and is expected on 20 October | 28天 / 28 days | 21天 / 21 days
23 | [8 empty] | 仪表 / Instruments | 1.压力： 1. Pressure: 评估无异常，客户现场提出； assessment shows no issue; raised by the customer on site 2.温度：不涉及 2. Temperature: not applicable 3.pH计: 3. pH: 不涉及 not applicable 4.差压/雷达/音叉：雷达无问题，差压液位计取消根部阀门 4. Differential pressure / radar / tuning fork: radar is acceptable; the root valve of the differential-pressure level transmitter is deleted | 提变更拆除现场阀门 / Raise a change to remove the valve on site |  | 2天 / 2 days
24 | [8 empty] | 泵 / Pumps | 评估无异常，客户现场提出； / Assessment shows no issue; raised by the customer on site | 四元隔膜泵-同步采购中 / Four-head diaphragm pumps – being purchased in parallel
25 | [8 empty] | 阀门 / Valves | 评估无异常，客户现场提出； / Assessment shows no issue; raised by the customer on site | 1、罐上口阀门需核实尺寸数量 1. The size and quantity of the valves on the tank top have to be verified 2、BPE管路已采购，预计10月20号到货 2. The BPE piping is purchased and is expected on 20 October | 28天 / 28 days | 21天 / 21 days
26 |  | 1211-HPPC03-T03 | 流动相A储罐（不带夹套） / Mobile phase A storage tank (non-jacketed) | 有效容积1000L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 1000 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 流动相A / Mobile phase A | 台 / unit | 1 | 设备本体 / Equipment body | 1.搅拌：不涉及 1. Agitator: not applicable 2.上口：部分罐口不满足2D： 2. Top nozzles: some nozzles do not meet 2D: 3.下口：罐口不满足２D：需求 3. Bottom nozzle: nozzle does not meet the 2D requirement 4.侧口：罐口不满足２D：需求 4. Side nozzles: nozzles do not meet the 2D requirement |  |  |  | 5d（验证4d+清洗1d） / 5 d (qualification 4 d + cleaning 1 d)
27 | [8 empty] | 管路 / Piping | 1.氮气：根部球阀-需要更换为隔膜阀； 1. Nitrogen: root ball valve – to be replaced by a diaphragm valve; 2.尾气：根部球阀-需要更换为隔膜阀； 2. Off-gas: root ball valve – to be replaced by a diaphragm valve; 3.溶剂：不涉及 3. Solvent: not applicable 4.物料 4. Material 4.1 1211-HPPC03-T03-P01 各流动相经静态混合器后进料管线; 4.1 1211-HPPC03-T03-P01 charging line for the mobile phases downstream of the static mixer; 更换为BPE管路，死角，排净;（做死角评估） change to BPE piping; dead legs and drainability (dead-leg assessment to be carried out) 4.2 1211-HPPC03-T03-P05 泵1318-HPPC03-T03-P02出口至T03储罐循环管线 4.2 1211-HPPC03-T03-P05 recirculation line from the outlet of pump 1318-HPPC03-T03-P02 to tank T03 更换为BPE管路，死角，排净;（做死角评估） change to BPE piping; dead legs and drainability (dead-leg assessment to be carried out) 4.3 T03储罐下口至泵1211-HPPC03-T03-P01入口管线 4.3 Line from the T03 tank bottom outlet to the inlet of pump 1211-HPPC03-T03-P01 更换为BPE管路，死角，排净;（做死角评估） change to BPE piping; dead legs and drainability (dead-leg assessment to be carried out) 4.4 T03储罐下口至泵1211-HPPC03-T03-P02入口管线 4.4 Line from the T03 tank bottom outlet to the inlet of pump 1211-HPPC03-T03-P02 更换为BPE管路，死角，排净;（做死角评估） change to BPE piping; dead legs and drainability (dead-leg assessment to be carried out) | BPE管路、隔膜阀已采购，已下单，预计10月中开始施工 The BPE piping and diaphragm valves are purchased and ordered; construction is expected to start in mid-October | 28天 / 28 days | 21天 / 21 days
28 | [8 empty] | 仪表 / Instruments | 1.压力： 1. Pressure: 取消根部阀-保证2D安装 delete the root valve – keep a 2D installation 2.温度： 2. Temperature: 不涉及 not applicable 3.pH计 3. pH: : 需要更换为在线进行替换校准的形式，新仪表形式采购询价中； has to be changed to a type that can be exchanged and calibrated in-line; quotations for the new instrument type are being obtained 4.差压/雷达/音叉：雷达无问题，差压液位计取消根部阀门 4. Differential pressure / radar / tuning fork: radar is acceptable; the root valve of the differential-pressure level transmitter is deleted | PH已经采购，更换安装套管，正在确认样式 The pH instrument is purchased; the mounting sleeve is being replaced and the design is being confirmed |  | 2天 / 2 days
29 | [8 empty] | 泵 / Pumps | 1211-HPPC03-T03-P02 按照BPE更换 replace to BPE standard | 离心泵已采购下单，预计10月下旬到货 The centrifugal pumps are purchased and ordered; delivery is expected in the second half of October | 35天 / 35 days
30 | [8 empty] | 阀门 / Valves | 自动球阀需要更换自动阀门隔膜阀--2D要求安装 The automated ball valves have to be replaced by automated diaphragm valves – installed to the 2D requirement XV-HPPC03-T03-P01-02 XV-HPPC03-T03-P01-03 XV-HPPC03-T03-P01-04 XV-HPPC03-T03-01 | 316L隔膜阀已采购，预计10月20号到货 The 316L diaphragm valves are purchased and are expected on 20 October 自控球阀预算已提报，为确认供应商，货期8周 The budget for the automated ball valves has been submitted; the supplier is not yet confirmed, lead time 8 weeks | 28天 28 days 56天 56 days | 21天 / 21 days
31 |  | 1211-HPPC03-T04 | 流动相B储罐（不带夹套） / Mobile phase B storage tank (non-jacketed) | 有效容积1000L，工作温度-20~100℃，工作压力-0.098~0.099MPa Working volume 1000 L, operating temperature −20 to 100 °C, operating pressure −0.098 to 0.099 MPa | SS316L | 乙腈 / Acetonitrile | 台 / unit | 1 | 设备本体 / Equipment body | 1.搅拌：不涉及 1. Agitator: not applicable 2.上口：部分罐口不满足2D： 2. Top nozzles: some nozzles do not meet 2D: 3.下口：罐口不满足２D：需求 3. Bottom nozzle: nozzle does not meet the 2D requirement 4.侧口：罐口不满足２D：需求 4. Side nozzles: nozzles do not meet the 2D requirement | BPE管路、隔膜阀已采购，已下单，预计10月中开始施工 The BPE piping and diaphragm valves are purchased and ordered; construction is expected to start in mid-October | 30+20 |  | 5d（验证4d+清洗1d） / 5 d (qualification 4 d + cleaning 1 d)
32 | [8 empty] | 管路 / Piping | 1.氮气：根部球阀-需要更换为隔膜阀； 1. Nitrogen: root ball valve – to be replaced by a diaphragm valve; 2.尾气：根部球阀-需要更换为隔膜阀； 2. Off-gas: root ball valve – to be replaced by a diaphragm valve; 3.溶剂： 3. Solvent: 3.1新鲜乙腈进料管线 3.1 Fresh acetonitrile charging line 4.物料 4. Material 4.1 1211-HPPC03-T04-P01 各流动相混合经静态混合器进料管线 4.1 1211-HPPC03-T04-P01 charging line for the mixed mobile phases via the static mixer 更换为BPE管路，死角，排净;（做死角评估） change to BPE piping; dead legs and drainability (dead-leg assessment to be carried out) 4.2 泵1211-HPPC03-T04-P01出口至T04储罐循环管线 4.2 Recirculation line from the outlet of pump 1211-HPPC03-T04-P01 to tank T04 更换为BPE管路，死角，排净;（做死角评估） change to BPE piping; dead legs and drainability (dead-leg assessment to be carried out) 4.3 1211-HPPC03-T04-P02 T04储罐下口至泵1211-HPPC03-T04-P01入口管线 4.3 1211-HPPC03-T04-P02 line from the T04 tank bottom outlet to the inlet of pump 1211-HPPC03-T04-P01 更换为BPE管路，死角，排净;（做死角评估） change to BPE piping; dead legs and drainability (dead-leg assessment to be carried out) | BPE管路、隔膜阀已采购，已下单，预计10月中开始施工 The BPE piping and diaphragm valves are purchased and ordered; construction is expected to start in mid-October | 28天 / 28 days | 21天 / 21 days
33 | [8 empty] | 仪表 / Instruments | 1.压力： 1. Pressure: 取消根部阀-保证2D安装 delete the root valve – keep a 2D installation 2.温度： 2. Temperature: 不涉及 not applicable 3.pH计 3. pH: : 需要更换为在线进行替换校准的形式，新仪表形式采购询价中； has to be changed to a type that can be exchanged and calibrated in-line; quotations for the new instrument type are being obtained 4.差压/雷达/音叉：雷达无问题，差压液位计取消根部阀门 4. Differential pressure / radar / tuning fork: radar is acceptable; the root valve of the differential-pressure level transmitter is deleted | PH已经采购，更换安装套管，正在确认样式 The pH instrument is purchased; the mounting sleeve is being replaced and the design is being confirmed |  | 2天 / 2 days
34 | [8 empty] | 泵 / Pumps | 不涉及 / Not applicable | N/A
35 | [8 empty] | 阀门 / Valves | 自动球阀需要更换自动阀门隔膜阀--2D要求安装 The automated ball valves have to be replaced by automated diaphragm valves – installed to the 2D requirement XV-HPPC03-T04-P01-02 XV-HPPC03-T04-P01-03 XV-HPPC03-T04-P01-04 XV-HPPC03-T04-01 | 316L隔膜阀已采购，预计10月20号到货 The 316L diaphragm valves are purchased and are expected on 20 October 自控球阀预算已提报，为确认供应商，货期8周 The budget for the automated ball valves has been submitted; the supplier is not yet confirmed, lead time 8 weeks | 28天 28 days 56天 56 days | 21天 / 21 days
36 |  | 其他 / Other | 质量流量计（快开、BPE） / Mass flow meter (quick-connect, BPE) | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 调整安装角度，保证安装可排尽，就近接收设备安装。何必在BPE管路改造中，同步整改。 Adjust the installation angle so that the installation is drainable and the receiving equipment is installed close by. To be rectified together with the BPE piping retrofit. | 确认现场条件进行角度调整 / Confirm the site conditions and adjust the angle | 0 |  | 3d（2天钝化+验证1d） / 3 d (passivation 2 d + qualification 1 d)
37 | [8 empty] | 现有已安装设备 / Existing installed equipment | 需要在氮气管路上增加双阀控，阀门类型需要同客户确认（其他公用工程阀门同步确认） A double valve arrangement has to be added on the nitrogen line; the valve type has to be agreed with the customer (the valves of the other utilities are confirmed at the same time) | 阀门预算已提报，未确认供应商；2片式货期15天，锻造式40天； The valve budget has been submitted; the supplier is not yet confirmed; lead time 15 days for the two-piece type and 40 days for the forged type
38 |  |  | 压力 / Pressure instrument | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 跟尾气口单独分开进行安装，合并在储罐及BPE管路整改中。 Install separately from the off-gas nozzle; included in the storage tank and BPE piping rectification. | 现场制定详细方案 / A detailed concept will be defined on site
39 | 制备系统 / Preparation system | 1211-HPPC03 | 高压制备系统 / High-pressure preparative (prep-HPLC) system | ADC1000 |  |  |  |  | 设备本体 / Equipment body | 1.客户对现有丝扣结构、卡套结构不满足，需要更换为快开结构；厂家评估涉及到高压管路不建议使用；BPE管路耐压0.7Mpa，制备系统运行7MPa，设计10Mpa，不满足使用要求。 1. The customer does not accept the existing threaded and compression-fitting connections and requires quick-connect fittings; the vendor's assessment is that this is not recommended for high-pressure piping: BPE piping is rated for 0.7 MPa while the preparative system operates at 7 MPa with a design pressure of 10 MPa, so it does not meet the requirement. 2.本体球阀为半包结构，需要更换为全包结构。--采购计划替换。 2. The ball valves on the unit are of the partly encapsulated type and have to be replaced by fully encapsulated ones – replacement is planned via procurement. 3.组分收集桶需要增加侧壁取样，需要增加。 3. Side-wall sampling has to be added to the fraction collection drums. | 1.需要跟客户将评估的内容进行解释。 1. The assessment has to be explained to the customer. 2.全包阀门已经采购，到货后10/15/2026进行更换 2. The fully encapsulated valves are purchased and will be replaced on 10/15/2026 after delivery 3.配置取样阀，桶进行改造。10/20/2026 3. Fit sampling valves and modify the drums. 10/20/2026
40 | [8 empty] | 管路 / Piping | 1.氮气：评估无异常，客户现场提出； 1. Nitrogen: assessment shows no issue; raised by the customer on site 2.尾气：评估无异常，客户现场提出； 2. Off-gas: assessment shows no issue; raised by the customer on site 3.溶剂：不涉及 3. Solvent: not applicable 4.物料： 4. Material: 4.1.制备到制备接收桶：1211-HPPC03-P01~P10非BPE管路-后续全部改造为BPE标准的管道重新制作； 4.1 From the preparative system to the receiving drums: 1211-HPPC03-P01 to P10 are non-BPE lines – all to be rebuilt to BPE standard later 4.2.1211-HPPC03-P11,非BPE管路，整体管路阀门较多，三通等不满足最小死角，后续改造BPE管路重新制作，不满足最小死角的更换T阀。 4.2 1211-HPPC03-P11 is a non-BPE line with many valves; the tees and similar do not meet the minimum dead-leg requirement, so the line will be rebuilt as BPE piping and the non-compliant points replaced by T-valves. 4.3.139788-step3A-P06到AT06管路，非BPE管路，整体管路阀门较多，三通等不满足最小死角，后续改造BPE管路重新制作，不满足最小死角的更换T阀。 4.3 139788-step3A-P06 to AT06 is a non-BPE line with many valves; the tees and similar do not meet the minimum dead-leg requirement, so the line will be rebuilt as BPE piping and the non-compliant points replaced by T-valves. 4.4 增加一根匀浆罐的固定BPE管道； 4.4 Add one fixed BPE line for the homogenisation vessel | 4.BPE管路配件已经采购，需要更换的T阀门重新采购，预计10/15/2026进行改造施工 4. The BPE piping components are purchased; the T-valves that have to be replaced are being re-ordered; the modification work is expected on 10/15/2026
41 | [8 empty] | 仪表 / Instruments | 1.压力：评估无异常，客户现场提出； 1. Pressure: assessment shows no issue; raised by the customer on site 2.温度：评估无异常，客户现场提出； 2. Temperature: assessment shows no issue; raised by the customer on site | N/A
42 | [8 empty] | 泵 / Pumps | 设备本体上三台三泵头高压泵：缺少排尽，需要沟通厂家是否可以改造； The three three-head high-pressure pumps on the unit lack drain points; it has to be discussed with the vendor whether they can be modified; 设备组分一台转移合格组分，一台转移废液，评估无异常，客户现场没有指出问题； One unit transfers in-spec fractions and one transfers waste liquid; assessment shows no issue and the customer raised no point on site | 明天咨询厂家技术看是否可以改在排净 Ask the vendor's technical team tomorrow whether a drain can be added
43 | [8 empty] | 阀门 / Valves | 高压制备存在非全部包裹的球阀，需要更换为全包球阀。 The high-pressure preparative system has ball valves that are not fully encapsulated; they have to be replaced by fully encapsulated ball valves. | 全包阀门已经采购，预计10/10/2026到货，更换周期2周 The fully encapsulated valves are purchased and are expected on 10/10/2026; the replacement takes 2 weeks
44 |  | 1211-HPPC03-AT03 | 组分接收搅拌罐（带夹套） / Fraction receiving agitated vessel (jacketed) | 1、有效容积8000L； 1. Working volume 8000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：316L不锈钢； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 设备本体 / Equipment body | 1.搅拌：全焊接结构，不存在螺丝的情况，可满足。 1. Agitator: fully welded design without screws, acceptable. 2.上口：氮气口、尾气压力表口、淋洗口两处、乙腈口、合格组分口、接管不满足最小死角的要求，需要更换T型阀及BPE管路。一处未使用的快开蝶阀需要拆除。 2. Top nozzles: nitrogen port, off-gas / pressure gauge port, two spray ports, acetonitrile port, in-spec fraction port – the connections do not meet the minimum dead-leg requirement, so T-valves and BPE piping have to be fitted. One unused quick-connect butterfly valve has to be removed. 3.下口：快开直口，评估无异常，客户未指出。 3. Bottom nozzle: straight quick-connect nozzle; assessment shows no issue and the customer raised no point. 4.侧口：音叉口，不满足2D要求，需要焊接封堵，更改为上插形式；pH计口，不满足2D需要焊接封堵； 4. Side nozzles: the tuning-fork port does not meet 2D and has to be welded closed, with the instrument changed to a top-inserted design; the pH port does not meet 2D and has to be welded closed. | 2和4项进行10/15/2026改造时进行改造， Items 2 and 4 will be modified during the 10/15/2026 works, 变径评估执行方式 the execution method for the reducers is being assessed 音叉液位计需要重新采购符合2D new tuning-fork level switches meeting 2D have to be purchased 管口改造方式需要与厂家开会确认方案 the nozzle modification method has to be confirmed with the vendor in a meeting
45 | [8 empty] | 管路 / Piping | 1.氮气：氮气管路评估满足，客户现场未指出。 1. Nitrogen: the nitrogen piping is assessed as compliant and the customer raised no point. 2.尾气：氮气管路评估满足，客户现场未指出。 2. Off-gas: the piping is assessed as compliant and the customer raised no point. 3.溶剂：氮气管路评估满足，客户现场未指出。 3. Solvent: the piping is assessed as compliant and the customer raised no point. 4.物料： 4. Material: 4.1：1211-HPPC03-AT03-P01乙腈管路，存在法兰调节阀，进行采购快开调节阀进行替换。 4.1 1211-HPPC03-AT03-P01 acetonitrile line: there is a flanged control valve; a quick-connect control valve will be purchased as a replacement. 4.2：1211-HPPC03-AT03-P02自循环管路，非BPE管路，需要更换为BPE管路，存在死角，需要更换为T型阀，控制最小死角； 4.2 1211-HPPC03-AT03-P02 recirculation line: non-BPE piping, has to be changed to BPE piping; dead legs are present and T-valves have to be fitted to control the minimum dead leg; 4.3：139788-step3A-P05 组分转移管路AT04：非BPE管路，需要更换为BPE管路，存在死角，需要更换为T型阀，控制最小死角； 4.3 139788-step3A-P05 fraction transfer line to AT04: non-BPE piping, has to be changed to BPE piping; dead legs are present and T-valves have to be fitted to control the minimum dead leg; 4.4：139788-step3A-P09组分转移到超滤管路：存在死角，需要更换为T型阀，控制最小死角； 4.4 139788-step3A-P09 fraction transfer line to ultrafiltration: dead legs are present and T-valves have to be fitted to control the minimum dead leg; | 4.BPE的管路配件已经购买 4. The BPE piping components are purchased 新识别的快开调节阀和T型阀，需要重新采购 The newly identified quick-connect control valves and T-valves have to be re-ordered 预计10/15/2026进行改造 The modification is expected on 10/15/2026 | 28天 / 28 days | 21天 / 21 days
46 | [8 empty] | 仪表 / Instruments | 1.压力：评估无异常，客户现场未指出； 1. Pressure: assessment shows no issue; the customer raised no point on site 2.温度： 2. Temperature: 评估无异常，客户现场未指出； assessment shows no issue; the customer raised no point on site 3.pH计 3. pH: ：需要更换为在线进行替换校准的形式，新仪表形式采购询价中； has to be changed to a type that can be exchanged and calibrated in-line; quotations for the new instrument type are being obtained 4.差压/雷达/音叉：音叉口不满足2D需要更换为上插形式，同时原音叉口封堵。 4. Differential pressure / radar / tuning fork: the tuning-fork port does not meet 2D, so the instrument has to be changed to a top-inserted design and the original port has to be welded closed. 5.质量流量计满足使用要求，无死角残留 5. The mass flow meter meets the requirement, with no hold-up | 3.寻找满足客户要求的PH。4.后续重新购买音叉液位计 3. Sourcing a pH instrument that meets the customer's requirement. 4. New tuning-fork level switches will be purchased later 10/15/2026进行改造。 Modification on 10/15/2026.
47 | [8 empty] | 泵 / Pumps | 1211-HPPC03-AT03-P01：自循环及转移到AT04储罐的气动隔膜泵，需要更换为卫生级离心泵。 1211-HPPC03-AT03-P01: the pneumatic diaphragm pump used for recirculation and transfer to tank AT04 has to be replaced by a sanitary centrifugal pump. 1211-HPPC03-AT03-P01：合格体系转移到超滤泵，目前隔膜泵无法排空，需要更换为卫生级离心泵。 1211-HPPC03-AT03-P01: the pump transferring the in-spec pool to ultrafiltration is a diaphragm pump that cannot be drained and has to be replaced by a sanitary centrifugal pump. 同客户确认该泵是否满足使用？ To be confirmed with the customer whether this pump is acceptable. | 离心泵已经采购，预计10月下旬到货后，10/15/2026开始改造安装 The centrifugal pumps are purchased; delivery is expected in the second half of October, and the modification and installation start on 10/15/2026 | 35天 / 35 days | 21天 / 21 days
48 | [8 empty] | 阀门 / Valves | 全部为隔膜阀，满足要求。 / All are diaphragm valves and meet the requirement. | N/A
49 |  | 1211-HPPC03-AT04 | 上样罐（带夹套） / Loading vessel (jacketed) | 1、有效容积3000L； 1. Working volume 3000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：316L不锈钢； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂等 / Various organic solvents | 台 / unit | 2 | 设备本体 / Equipment body | 1.搅拌：全焊接的形式，满足要求。 1. Agitator: fully welded design, meets the requirement. 2.上口：淋洗球口两个，尾气口1个、预留口1个，压力变送器口一个、氮气口1个；乙腈口一个，存在阀门下变径情况，不满足2D需要更换BPE管路进行； 2. Top nozzles: two spray ball ports, one off-gas port, one spare port, one pressure transmitter port, one nitrogen port and one acetonitrile port; there is a reducer below the valve, which does not meet 2D, so BPE piping has to be fitted; 3.下口：快开直口的形式，评估无异常，客户现场未指出。 3. Bottom nozzle: straight quick-connect design; assessment shows no issue and the customer raised no point on site. 4.侧口：音叉口不满足2D及在线更换的形式，需要更换音叉为上插入的形式，原有音叉口封堵。 4. Side nozzles: the tuning-fork port does not meet 2D and does not allow in-line exchange, so the instrument has to be changed to a top-inserted design and the original port has to be welded closed. | 2和4项进行10/15/2026改造时进行改造， Items 2 and 4 will be modified during the 10/15/2026 works, 变径评估执行方式 the execution method for the reducers is being assessed 音叉液位计需要重新采购符合2D new tuning-fork level switches meeting 2D have to be purchased 管口改造方式需要与厂家开会确认方案 the nozzle modification method has to be confirmed with the vendor in a meeting | 0 |  | 4d（钝化1天+验证2d+清洗1d） 4 d (passivation 1 d + qualification 2 d + cleaning 1 d)
50 | [8 empty] | 管路 / Piping | 1.氮气：氮气管路评估满足，客户现场未指出。 1. Nitrogen: the nitrogen piping is assessed as compliant and the customer raised no point. 2.尾气：氮气管路评估满足，客户现场未指出。 2. Off-gas: the piping is assessed as compliant and the customer raised no point. 3.溶剂：氮气管路评估满足，客户现场未指出。 3. Solvent: the piping is assessed as compliant and the customer raised no point. 4.物料： 4. Material: 4.1：1211-HPPC03-AT04-P01，乙腈管路，存在法兰调节阀，进行采购快开调节阀进行替换。 4.1 1211-HPPC03-AT04-P01 acetonitrile line: there is a flanged control valve; a quick-connect control valve will be purchased as a replacement. 4.2：纯水管路，需要增加润洗排尽及T型阀三通。 4.2 Purified-water line: rinsing / drain points and a T-valve tee have to be added. 4.3：1211-HPPC03-AT04-P02上样管路，非BPE管路，需要更换为BPE管路，同时进行死角三通等更换，确保满足最小死角要求。 4.3 1211-HPPC03-AT04-P02 loading line: non-BPE piping, has to be changed to BPE piping, and dead-leg tees and similar have to be replaced to meet the minimum dead-leg requirement. 4.4：1211-HPPC03-AT04-P03自循环管路，非BPE管路，需要更换为BPE管路，同时进行死角三通等更换，确保满足最小死角要求。 4.4 1211-HPPC03-AT04-P03 recirculation line: non-BPE piping, has to be changed to BPE piping, and dead-leg tees and similar have to be replaced to meet the minimum dead-leg requirement. | 4.BPE的管路配件已经购买 4. The BPE piping components are purchased 新识别的快开调节阀和T型阀，需要重新采购 The newly identified quick-connect control valves and T-valves have to be re-ordered 预计10/15/2026进行改造 The modification is expected on 10/15/2026 | 28天 / 28 days | 21天 / 21 days
51 | [8 empty] | 仪表 / Instruments | 1.压力：评估无异常，客户现场未指出； 1. Pressure: assessment shows no issue; the customer raised no point on site 2.温度： 2. Temperature: 评估无异常，客户现场未指出； assessment shows no issue; the customer raised no point on site 3.pH计 3. pH: ：需要更换为在线进行替换校准的形式，新仪表形式采购询价中 has to be changed to a type that can be exchanged and calibrated in-line; quotations for the new instrument type are being obtained 4.差压/雷达/音叉：音叉口测入，需要更换为顶部插入。 4. Differential pressure / radar / tuning fork: the tuning fork is side-inserted and has to be changed to top-inserted. | 3.寻找满足客户要求的PH。4.后续重新购买音叉液位计 3. Sourcing a pH instrument that meets the customer's requirement. 4. New tuning-fork level switches will be purchased later 10/15/2026进行改造。 Modification on 10/15/2026.
52 | [8 empty] | 泵 / Pumps | 1211-HPPC03-AT04-P01一台气动隔膜泵，用于自循环清洗，无法排空，需要更换为离心泵。 1211-HPPC03-AT04-P01: one pneumatic diaphragm pump used for recirculation cleaning cannot be drained and has to be replaced by a centrifugal pump. | 离心泵已经采购，预计10月下旬到货后，10/15/2026开始改造安装 The centrifugal pumps are purchased; delivery is expected in the second half of October, and the modification and installation start on 10/15/2026 | 35天 / 35 days | 21天 / 21 days
53 | [8 empty] | 阀门 / Valves | 全部为隔膜阀，满足要求。 / All are diaphragm valves and meet the requirement. | N/A
54 |  | 1211-HPPC03-AT05 | 组分收集罐 / Fraction collection vessel | "1、有效容积3000L； "1. Working volume 3000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa；" 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa;" |  |  |  |  | 设备本体 / Equipment body | 1.搅拌：搅拌存在螺丝结构，需要厂家到场进行动火焊接。 1. Agitator: the agitator has bolted parts, so the vendor has to come on site for hot-work welding. 2.上口：淋洗球口两个，尾气口1个、预留口1个，压力变送器口一个、氮气口1个；乙腈口一个，存在阀门下变径情况，不满足2D需要更换BPE管路进行；缺少固体加料口一个，需要进行动火改造增加； 2. Top nozzles: two spray ball ports, one off-gas port, one spare port, one pressure transmitter port, one nitrogen port and one acetonitrile port; there is a reducer below the valve, which does not meet 2D, so BPE piping has to be fitted; one solids charging port is missing and has to be added by hot-work modification; 3.下口：快开直口的形式，评估无异常，客户现场未指出。 3. Bottom nozzle: straight quick-connect design; assessment shows no issue and the customer raised no point on site. 4.侧口：音叉口不满足2D及在线更换的形式，需要采购新形式的音叉进行更换。 4. Side nozzles: the tuning-fork port does not meet 2D and does not allow in-line exchange, so a new type of tuning-fork instrument has to be purchased as a replacement. | 2和4项进行10/15/2026改造时进行改造， Items 2 and 4 will be modified during the 10/15/2026 works, 变径评估执行方式 the execution method for the reducers is being assessed 音叉液位计需要重新采购符合2D new tuning-fork level switches meeting 2D have to be purchased 管口改造方式需要与厂家开会确认方案 the nozzle modification method has to be confirmed with the vendor in a meeting | 0
55 | [8 empty] | 管路 / Piping | 1.氮气：氮气管路评估满足，客户现场未指出。 1. Nitrogen: the nitrogen piping is assessed as compliant and the customer raised no point. 2.尾气：氮气管路评估满足，客户现场未指出。 2. Off-gas: the piping is assessed as compliant and the customer raised no point. 3.溶剂：氮气管路评估满足，客户现场未指出。 3. Solvent: the piping is assessed as compliant and the customer raised no point. 4.物料： 4. Material: 4.1：1211-HPPC03-AT05-P01，存在法兰调节阀，进行采购快开调节阀进行替换。 4.1 1211-HPPC03-AT05-P01: there is a flanged control valve; a quick-connect control valve will be purchased as a replacement. 4.2：纯水管路，需要增加润洗排尽及T型阀三通。 4.2 Purified-water line: rinsing / drain points and a T-valve tee have to be added. 4.3：139788-step3A-P04，自循环及去AT03管路，非BPE管路，需要更换为BPE管路，同时进行死角三通等更换，确保满足最小死角要求。 4.3 139788-step3A-P04, the recirculation line and the line to AT03: non-BPE piping, has to be changed to BPE piping, and dead-leg tees and similar have to be replaced to meet the minimum dead-leg requirement. | 4.BPE的管路配件已经购买 4. The BPE piping components are purchased 新识别的快开调节阀和T型阀，需要重新采购 The newly identified quick-connect control valves and T-valves have to be re-ordered 预计10/15/2026进行改造 The modification is expected on 10/15/2026 | 28天 / 28 days | 21天 / 21 days
56 | [8 empty] | 仪表 / Instruments | 1.压力：评估无异常，客户现场未指出； 1. Pressure: assessment shows no issue; the customer raised no point on site 2.温度： 2. Temperature: 评估无异常，客户现场未指出； assessment shows no issue; the customer raised no point on site 3.pH计 3. pH: ：需要更换为在线进行替换校准的形式，新仪表形式采购询价中； has to be changed to a type that can be exchanged and calibrated in-line; quotations for the new instrument type are being obtained 4.差压/雷达/音叉：音叉口不满足2D及在线更换的形式，需要更换音叉为上插入的形式，原有音叉口封堵。 4. Differential pressure / radar / tuning fork: the tuning-fork port does not meet 2D and does not allow in-line exchange, so the instrument has to be changed to a top-inserted design and the original port has to be welded closed. | 3.寻找满足客户要求的PH。4.后续重新购买音叉液位计 3. Sourcing a pH instrument that meets the customer's requirement. 4. New tuning-fork level switches will be purchased later 10/15/2026进行改造。 Modification on 10/15/2026.
57 | [8 empty] | 泵 / Pumps | 1211-HPPC03-AT05-P01：需要由气动隔膜阀更换为离心泵。 1211-HPPC03-AT05-P01: the pneumatic diaphragm pump has to be replaced by a centrifugal pump. | 离心泵已经采购，预计10月下旬到货后，10/15/2026开始改造安装 The centrifugal pumps are purchased; delivery is expected in the second half of October, and the modification and installation start on 10/15/2026 | 35天 / 35 days | 21天 / 21 days
58 | [8 empty] | 阀门 / Valves | 全部为隔膜阀，满足使用需求。 / All are diaphragm valves and meet the requirement. | N/A
59 |  | 1211-HPPC03-AT06 | 1000L组分收集罐 / 1000 L fraction collection vessel | 1000L |  |  |  |  | 设备本体 / Equipment body | 1.搅拌：全焊接的形式，满足要求。 1. Agitator: fully welded design, meets the requirement. 2.上口：淋洗球口两个，尾气压力变送器口一个、氮气口1个；乙腈口一个，纯水口一个，合格组分口一个，存在阀门下变径情况，不满足2D需要更换BPE管路进行；同时需要增加一个口进行单独安装压力表，需要现场动火改造进行增加； 2. Top nozzles: two spray ball ports, one off-gas / pressure transmitter port, one nitrogen port, one acetonitrile port, one purified-water port and one in-spec fraction port; there is a reducer below the valve, which does not meet 2D, so BPE piping has to be fitted; in addition one port has to be added for a separate pressure gauge, which requires hot-work modification on site; 3.下口：快开直口的形式，评估无异常，客户现场未指出。 3. Bottom nozzle: straight quick-connect design; assessment shows no issue and the customer raised no point on site. 4.侧口：音叉口不满足2D及在线更换的形式，需要更换音叉为上插入的形式，原有音叉口封堵。差压口需要取消更换为雷达的形式去测量液位。 4. Side nozzles: the tuning-fork port does not meet 2D and does not allow in-line exchange, so the instrument has to be changed to a top-inserted design and the original port has to be welded closed. The differential-pressure port has to be deleted and the level measured by radar instead. | 2和4项进行10/15/2026改造时进行改造， Items 2 and 4 will be modified during the 10/15/2026 works, 变径评估执行方式 the execution method for the reducers is being assessed 音叉液位计需要重新采购符合2D new tuning-fork level switches meeting 2D have to be purchased 管口改造方式需要与厂家开会确认方案 the nozzle modification method has to be confirmed with the vendor in a meeting | 0
60 | [8 empty] | 管路 / Piping | 1.氮气：氮气管路评估满足，客户现场未指出。 1. Nitrogen: the nitrogen piping is assessed as compliant and the customer raised no point. 2.尾气：氮气管路评估满足，客户现场未指出。 2. Off-gas: the piping is assessed as compliant and the customer raised no point. 3.溶剂：氮气管路评估满足，客户现场未指出。 3. Solvent: the piping is assessed as compliant and the customer raised no point. 4.物料： 4. Material: 4.1：1211-HPPC03-AT06-P01，纯水管路，需要增加润洗排尽及T型阀三通。 4.1 1211-HPPC03-AT06-P01 purified-water line: rinsing / drain points and a T-valve tee have to be added. 4.2：1211-HPPC03-AT06-P02，自循环管路，非BPE管路，需要更换为BPE管路，同时进行死角三通等更换，确保满足最小死角要求。 4.2 1211-HPPC03-AT06-P02 recirculation line: non-BPE piping, has to be changed to BPE piping, and dead-leg tees and similar have to be replaced to meet the minimum dead-leg requirement. 4.3：139788-step3A-P07合格组分转移到AT03、AT03，非BPE管路，需要更换为BPE管路，同时进行死角三通等更换，确保满足最小死角要求。 4.3 139788-step3A-P07 transfer line for in-spec fractions to AT03: non-BPE piping, has to be changed to BPE piping, and dead-leg tees and similar have to be replaced to meet the minimum dead-leg requirement. | 4.BPE的管路配件已经购买 4. The BPE piping components are purchased 新识别的快开调节阀和T型阀，需要重新采购 The newly identified quick-connect control valves and T-valves have to be re-ordered 预计10/15/2026进行改造 The modification is expected on 10/15/2026 | 28天 / 28 days | 21天 / 21 days
61 | [8 empty] | 仪表 / Instruments | 1.压力：评估无异常，客户现场未指出； 1. Pressure: assessment shows no issue; the customer raised no point on site 2.温度： 2. Temperature: 评估无异常，客户现场未指出； assessment shows no issue; the customer raised no point on site 3.pH计 3. pH: ：需要更换为在线进行替换校准的形式，新仪表形式采购询价中； has to be changed to a type that can be exchanged and calibrated in-line; quotations for the new instrument type are being obtained 4.差压/雷达/音叉：音叉口不满足2D及在线更换的形式，需要更换音叉为上插入的形式，原有音叉口封堵。 4. Differential pressure / radar / tuning fork: the tuning-fork port does not meet 2D and does not allow in-line exchange, so the instrument has to be changed to a top-inserted design and the original port has to be welded closed. | 3.寻找满足客户要求的PH。4.后续重新购买音叉液位计 3. Sourcing a pH instrument that meets the customer's requirement. 4. New tuning-fork level switches will be purchased later 10/15/2026进行改造。 Modification on 10/15/2026.
62 | [8 empty] | 泵 / Pumps | 1211-HPPC03-AT06-P01，自循环及合格组分的转移，气动隔膜泵不满足排尽要求，更换更换为卫生级离心泵。 1211-HPPC03-AT06-P01: for recirculation and transfer of in-spec fractions the pneumatic diaphragm pump does not meet the drainability requirement and is replaced by a sanitary centrifugal pump. | 离心泵已经采购，预计10月下旬到货后，10/15/2026开始改造安装 The centrifugal pumps are purchased; delivery is expected in the second half of October, and the modification and installation start on 10/15/2026 | 35天 / 35 days | 21天 / 21 days
63 | [8 empty] | 阀门 / Valves | 全部为隔膜阀，满足需求 / All are diaphragm valves and meet the requirement | N/A
64 |  | 1211-HPPC03-T06 | 1000L顶样罐 / 1000 L top-sample vessel | 1000L |  |  |  |  | 设备本体 / Equipment body | 1.搅拌：无搅拌。 1. Agitator: none. 2.上口：淋洗球口1个、氮气口1个；乙腈口一个，温度插底口1个，雷达口一个，音叉口一个，压力及尾气口一个；不满足2D需要更换BPE管路进行；同时需要增加一个口进行单独安装压力表，需要现场动火改造进行增加； 2. Top nozzles: one spray ball port, one nitrogen port, one acetonitrile port, one temperature dip-tube port, one radar port, one tuning-fork port and one pressure / off-gas port; they do not meet 2D, so BPE piping has to be fitted; in addition one port has to be added for a separate pressure gauge, which requires hot-work modification on site; 3.下口：快开直口的形式，评估无异常，客户现场未指出。 3. Bottom nozzle: straight quick-connect design; assessment shows no issue and the customer raised no point on site. 4.侧口：未涉及。 4. Side nozzles: not applicable. | 10/15/2026改造时进行改造， To be modified during the 10/15/2026 works, 变径评估执行方式 the execution method for the reducers is being assessed 音叉液位计需要重新采购符合2D new tuning-fork level switches meeting 2D have to be purchased 管口改造方式需要与厂家开会确认方案 the nozzle modification method has to be confirmed with the vendor in a meeting | 0
65 | [8 empty] | 管路 / Piping | 1.氮气：氮气管路评估满足，客户现场未指出。 1. Nitrogen: the nitrogen piping is assessed as compliant and the customer raised no point. 2.尾气：氮气管路评估满足，客户现场未指出。 2. Off-gas: the piping is assessed as compliant and the customer raised no point. 3.溶剂：氮气管路评估满足，客户现场未指出。 3. Solvent: the piping is assessed as compliant and the customer raised no point. 4.物料： 4. Material: 4.1：1211-HPPC03-T06-P01自循环管路，非BPE管路，需要更换为BPE管路，同时进行死角三通等更换，确保满足最小死角要求。 4.1 1211-HPPC03-T06-P01 recirculation line: non-BPE piping, has to be changed to BPE piping, and dead-leg tees and similar have to be replaced to meet the minimum dead-leg requirement. 4.2：1211-HPPC03-T06-P02到AT04管路，非BPE管路，需要更换为BPE管路，同时进行死角三通等更换，确保满足最小死角要求。 4.2 1211-HPPC03-T06-P02 line to AT04: non-BPE piping, has to be changed to BPE piping, and dead-leg tees and similar have to be replaced to meet the minimum dead-leg requirement. 4.3：1211-HPPC03-T06-P03到制备系统，非BPE管路，需要更换为BPE管路，同时进行死角三通等更换，确保满足最小死角要求。 4.3 1211-HPPC03-T06-P03 line to the preparative system: non-BPE piping, has to be changed to BPE piping, and dead-leg tees and similar have to be replaced to meet the minimum dead-leg requirement. | 4.BPE的管路配件已经购买 4. The BPE piping components are purchased 新识别的快开调节阀和T型阀，需要重新采购 The newly identified quick-connect control valves and T-valves have to be re-ordered 预计10/15/2026进行改造 The modification is expected on 10/15/2026 | 28天 / 28 days | 21天 / 21 days
66 | [8 empty] | 仪表 / Instruments | 1.压力：与尾气口公用，不满足可清洗的要求，需更换1变2的阀门，见客户链接； 1. Pressure: shares a nozzle with the off-gas line, which does not meet the cleanability requirement; a 1-to-2 splitter valve has to be fitted, see the customer's link; 2.温度： 2. Temperature: 评估无异常，客户现场未指出； assessment shows no issue; the customer raised no point on site 3.差压/雷达/音叉：音叉口不满足2D及在线更换的形式，需要更换音叉为上插入的形式，原有音叉口封堵。 3. Differential pressure / radar / tuning fork: the tuning-fork port does not meet 2D and does not allow in-line exchange, so the instrument has to be changed to a top-inserted design and the original port has to be welded closed. 4.质量流量计需要侧装或者倒装，避免残留，需要重新调整安装角度。 4. The mass flow meter has to be side- or inverted-mounted to avoid hold-up, so the installation angle has to be readjusted. | 3.寻找满足客户要求的PH。4.后续重新购买音叉液位计 3. Sourcing a pH instrument that meets the customer's requirement. 4. New tuning-fork level switches will be purchased later 10/15/2026进行改造。 Modification on 10/15/2026.
67 | [8 empty] | 泵 / Pumps | 1211-HPPC03-T06-P01：自循环及顶样使用，非BPE管路，需要更换为BPE管路，同时进行死角三通等更换，确保满足最小死角要求。 1211-HPPC03-T06-P01: used for recirculation and top sampling; non-BPE piping, has to be changed to BPE piping, and dead-leg tees and similar have to be replaced to meet the minimum dead-leg requirement. | 离心泵已经采购，预计10月下旬到货后，10/15/2026开始改造安装 The centrifugal pumps are purchased; delivery is expected in the second half of October, and the modification and installation start on 10/15/2026 | 35天 / 35 days | 21天 / 21 days
68 | [8 empty] | 阀门 / Valves | C3储罐，可使用球阀，部分配置隔膜阀，满足使用需求。 Tank C3: ball valves may be used, some diaphragm valves are fitted, meets the requirement. | N/A
69 |  |  | 区域内的氮气管路阀门 / Nitrogen line valves inside the area | 单个快开截止阀 / Single quick-connect shut-off valve |  |  |  |  | 管路 / Piping | 需要在氮气管路上增加双阀控 / A double valve arrangement has to be added on the nitrogen line | 阀门购买中 / Valves being purchased
70 |  |  | BPE管道、管件 / BPE piping and fittings | 见附件 / See attachment | 316L | —— | 台 / unit | 见附件 / See attachment | 现有已安装设备 / Existing installed equipment | 整体管路2D标准，T型阀，最小死角，罐口位置重新改造。管路上的流体过滤器、变径等位置考虑可排尽。每一个Tank的溶液进来的口，都应该有个小排废口用于冲洗管路的时候在小排废口排出。 The whole line to 2D standard, with T-valves and minimum dead legs; the tank nozzle positions have to be reworked. Drainability has to be considered at the in-line filters, reducers and similar points. Every tank should have a small waste drain at the solution inlet nozzle so that the line can be drained there when it is flushed. | 确认现场条件进行角度调整，待IEPE出方案，工程确认施工，生产、QA共同确认方案可行。 Confirm the site conditions and adjust the angles; waiting for the IEPE concept, engineering confirmation of the works, and joint confirmation of feasibility by Production and QA. |  |  | 5d（2天钝化+验证2d+清洗1d） 5 d (passivation 2 d + qualification 2 d + cleaning 1 d)
71 | 超滤 / Ultrafiltration | 1211-TFF01 | 30㎡超滤 / 30 m² ultrafiltration skid | 30㎡ / 30 m² |  |  |  |  | 设备本体 / Equipment body | 1.超滤罐进行搅拌形式的同客户的讨论，是否变动为上搅拌。 1. Discuss the agitator design of the ultrafiltration vessel with the customer and whether it should be changed to a top-mounted agitator. 2. 现有0.6平的膜包约夹50块，客户提出有3平的膜包可以夹10块。我们需要联系赛多利斯询问3平的膜包(2kD)。 2. About 50 of the existing 0.6 m² cassettes are stacked; the customer mentioned that 10 cassettes of 3 m² could be used instead. We have to contact Sartorius about 3 m² cassettes (2 kD). 3. 在转子泵后进膜包组件前，加流量计。 3. Add a flow meter downstream of the rotary lobe pump and upstream of the cassette assembly. 4. 因客户担心倒吸导致物料损失：强烈建议把阀门V305去掉，或者保留V305但再加一条管路连到循环罐内（如图，照片上用红线圈出标号3）。 4. Because the customer is worried about product loss through back-suction: it is strongly recommended to delete valve V305, or to keep V305 but add another line back into the recirculation vessel (see photo, marked 3 with a red circle). 5. PID图中循环罐内左边的甲醇插底管需要往下插一些，插底管延长至液面往上一点点的位置（90L液位），液体需要打到循环罐壁上（如图，照片上用蓝线圈出标号5）。（客户担心滴甲醇的时候滴的量很少，同时也补氮气，甲醇会有挥发的风险） 5. In the P&ID the methanol dip tube on the left inside the recirculation vessel has to be inserted deeper, extended to just above the liquid level (90 L level), and the liquid has to be directed onto the wall of the recirculation vessel (see photo, marked 5 with a blue circle). (The customer is worried that the methanol is dosed in very small amounts while nitrogen is fed at the same time, creating a risk of evaporation.) | 待同客户确认 / To be confirmed with the customer
72 | [8 empty] | 管路 / Piping | 1.氮气：客户暂未到现场进行确认 1. Nitrogen: the customer has not been on site to confirm yet 2.尾气：客户暂未到现场进行确认 2. Off-gas: the customer has not been on site to confirm yet 3.溶剂：客户暂未到现场进行确认 3. Solvent: the customer has not been on site to confirm yet 4.物料：客户暂未到现场进行确认 4. Material: the customer has not been on site to confirm yet | 待同客户确认 / To be confirmed with the customer
73 | [8 empty] | 仪表 / Instruments | 1.压力： 1. Pressure: 客户暂未到现场进行确认 the customer has not been on site to confirm yet 2.温度：客户暂未到现场进行确认 2. Temperature: the customer has not been on site to confirm yet 3.pH计 3. pH: ：客户暂未到现场进行确认 the customer has not been on site to confirm yet 4.称重模块：客户暂未到现场进行确认 4. Load cells: the customer has not been on site to confirm yet 5.电导：客户暂未到现场进行确认 5. Conductivity: the customer has not been on site to confirm yet | 待同客户确认 / To be confirmed with the customer
74 | [8 empty] | 泵 / Pumps | 转子泵、四元隔膜泵满足需求； / The rotary lobe pump and the four-head diaphragm pump meet the requirement; | N/A
75 | [8 empty] | 阀门 / Valves | 全部为隔膜阀，满足使用需求。 / All are diaphragm valves and meet the requirement. | N/A
76 |  | 1211-TFF01-T01 | 超滤接收储罐（带夹套） / Ultrafiltration receiving storage tank (jacketed) | 1、有效容积1000L； 1. Working volume 1000 L; 2、罐内设计温度-20~150℃，夹套设计温度-25~180℃； 2. Vessel design temperature −20 to 150 °C, jacket design temperature −25 to 180 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | SS316L | 各类有机溶剂等 / Various organic solvents | 台 / unit | 1 | 设备本体 / Equipment body | 1.搅拌：无 1. Agitator: none 2.上口：均为快开口，部分不满足2D 2. Top nozzles: all quick-connect, some do not meet 2D 3.下口: 快开口，无问题 3. Bottom nozzle: quick-connect, no issue 4.侧口: 不满足2D，主要是差压口。 4. Side nozzles: do not meet 2D, mainly the differential-pressure port. | 储罐管口全部改为2D，与诚信确认方案和货期； All tank nozzles are converted to 2D; the concept and lead time are being confirmed with Chengxin; |  |  | 5d（验证4d+清洗1d） / 5 d (qualification 4 d + cleaning 1 d)
77 | [8 empty] | 管路 / Piping | 1.氮气：无问题 1. Nitrogen: no issue 2.尾气：无问题 2. Off-gas: no issue 3.溶剂：非BPE管路，需更换BPE管路 3. Solvent: non-BPE piping, has to be changed to BPE piping 4.物料：无问题，BPE管路，坡度也没问题 4. Material: no issue; BPE piping and the slope are also acceptable | BPE管路、隔膜阀已采购，已下单，预计10月中开始施工 The BPE piping and diaphragm valves are purchased and ordered; construction is expected to start in mid-October | 28天 / 28 days | 21天 / 21 days
78 | [8 empty] | 仪表 / Instruments | 1.压力： 1. Pressure: 同尾气一个口，需要进行调整或更换三通； shares one nozzle with the off-gas line; it has to be rearranged or a tee has to be fitted; 2.温度： 2. Temperature: 无问题； no issue; 3.pH计 3. pH: ：无； none; 4.差压/雷达/音叉：音叉、压差不满足BPE 2D要求 4. Differential pressure / radar / tuning fork: the tuning fork and the differential pressure do not meet the BPE 2D requirement | 取消压差，改为雷达，需重新采购雷达液位计 Delete the differential pressure and change to radar; new radar level transmitters have to be purchased
79 | [8 empty] | 泵 / Pumps | 无 / None | N/A
80 | [8 empty] | 阀门 / Valves | 溶剂管道阀门需更换BPE隔膜阀 The valves on the solvent piping have to be replaced by BPE diaphragm valves | 316L隔膜阀已采购，预计10月20号到货 The 316L diaphragm valves are purchased and are expected on 20 October | 28天 / 28 days | 21天 / 21 days
81 | 沉淀 / Precipitation | 1211-R01 | 析晶釜 / Crystallizer | 1、有效容积2000L； 1. Working volume 2000 L; 2、釜内设计温度-25~200℃，夹套设计温度-25~220℃； 2. Reactor design temperature −25 to 200 °C, jacket design temperature −25 to 220 °C; 3、釜内设计压力-0.1~0.4MPa；夹套工作压力0.6Mpa； 3. Reactor design pressure −0.1 to 0.4 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：304不锈钢衬C22或C276； Product contact: 304 stainless steel lined with C22 or C276; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、酸、碱等 / Various organic solvents, acids, bases, etc. | 台 / unit | 1 | 设备本体 / Equipment body | 1.搅拌：无问题 1. Agitator: no issue 2.上口：温度计口过长 2. Top nozzles: the thermometer nozzle is too long 3.下口：快开的形式，不满足2D 3. Bottom nozzle: quick-connect design, does not meet 2D 4.侧口：无 4. Side nozzles: none | BPE管路改造时同步调整。 / Adjusted together with the BPE piping retrofit. |  |  | 4d（钝化1天+验证2d+清洗1d） 4 d (passivation 1 d + qualification 2 d + cleaning 1 d)
82 | [8 empty] | 管路 / Piping | 1.氮气：釜口管路过长 1. Nitrogen: the reactor nozzle piping is too long 2.尾气：釜口管路过长 2. Off-gas: the reactor nozzle piping is too long 3.溶剂：釜口管路过长 3. Solvent: the reactor nozzle piping is too long 4.物料：不满足2D，下口为双三通 4. Material: does not meet 2D; the bottom outlet has a double tee | BPE管路改造时同步调整。 Adjusted together with the BPE piping retrofit. 变径形式需要确认方案 The reducer design has to be confirmed | 28天 / 28 days | 21天 / 21 days
83 | [8 empty] | 仪表 / Instruments | 1.压力： 1. Pressure: 非单独口，需更换为独立管口 no dedicated nozzle; a separate nozzle has to be fitted 2.温度：探头杆过长 2. Temperature: the probe stem is too long ，需更换温度计； , the thermometer has to be replaced; 3.pH计 3. pH: ：无 none 4.差压/雷达/音叉：无 4. Differential pressure / radar / tuning fork: none | 温度计已采购 The thermometer is purchased BPE管路改造时同步调整。 Adjusted together with the BPE piping retrofit. | 28天 / 28 days | 21天 / 21 days
84 | [8 empty] | 泵 / Pumps | 无 / None | N/A
85 | [8 empty] | 阀门 / Valves | 全部为隔膜阀，满足需求；溶剂管路球阀需要同客户确认是否按照CIP管路配置隔膜阀。 All are diaphragm valves and meet the requirement; for the ball valves on the solvent piping it has to be confirmed with the customer whether diaphragm valves are required as for CIP piping. | 重新采购1台气动快开隔膜阀 / Purchase one more pneumatic quick-connect diaphragm valve | 56天 / 56 days | 2
86 |  | 1211-AT01 | 搅拌罐 / Agitated vessel | 1、有效容积600L； 1. Working volume 600 L; 2、罐内设计温度-25~200℃，夹套设计温度-25~220℃； 2. Vessel design temperature −25 to 200 °C, jacket design temperature −25 to 220 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：316L不锈钢； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、盐溶液等 / Various organic solvents, salt solutions, etc. | 台 / unit | 1 | 设备本体 / Equipment body | 1.搅拌：无问题 1. Agitator: no issue 2.上口：不满足2D 2. Top nozzles: do not meet 2D 3.下口：不满足2D 3. Bottom nozzle: does not meet 2D 4.侧口：不满足2D，罐体大法兰密封为平垫密封，不满足要求 4. Side nozzles: do not meet 2D; the large vessel flange uses a flat gasket seal, which does not meet the requirement | 无法进行改造，计划使用东富龙或英德储罐，图纸索要中，后续核对。 Modification is not feasible; the plan is to use a Tofflon or Yingde tank; the drawings have been requested and will be checked. |  |  | 5d（验证4d+清洗1d） / 5 d (qualification 4 d + cleaning 1 d)
87 | [8 empty] | 管路 / Piping | 1.氮气：无问题 1. Nitrogen: no issue 2.尾气：无问题 2. Off-gas: no issue 3.溶剂：无问题 3. Solvent: no issue 4.物料：无问题 4. Material: no issue | N/A
88 | [8 empty] | 仪表 / Instruments | 1.压力： 1. Pressure: 非单独口 no dedicated nozzle 2.温度： 2. Temperature: 不满足2D does not meet 2D 3.pH计 3. pH: ：无 none 4.差压/雷达/音叉：压差、雷达不满足2D 4. Differential pressure / radar / tuning fork: differential pressure and radar do not meet 2D | BPE管路改造时同步调整。 Adjusted together with the BPE piping retrofit. 变径形式需要确认方案 The reducer design has to be confirmed | 28天 / 28 days | 21天 / 21 days
89 | [8 empty] | 泵 / Pumps | 计量泵不满足排尽要求，计划更换为四元隔膜泵； The metering pump does not meet the drainability requirement and is planned to be replaced by a four-head diaphragm pump; | BPE管路改造时同步调整。 Adjusted together with the BPE piping retrofit. 变径形式需要确认方案，部分管口管件太小买不到，与厂家沟通 The reducer design has to be confirmed; some nozzles and fittings are too small to buy, and this is being discussed with the vendor | 28天 / 28 days | 21天 / 21 days
90 | [8 empty] | 阀门 / Valves | 全部为隔膜阀，满足需求 / All are diaphragm valves and meet the requirement | N/A
91 |  | 1211-AT02 | 搅拌罐 / Agitated vessel | 1、有效容积80L； 1. Working volume 80 L; 2、罐内设计温度-25~200℃，夹套设计温度-25~220℃； 2. Vessel design temperature −25 to 200 °C, jacket design temperature −25 to 220 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：316L不锈钢； Product contact: 316L stainless steel; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、酸、碱等 / Various organic solvents, acids, bases, etc. | 台 / unit | 1 | 设备本体 / Equipment body | 计划更换储罐： The tank is planned to be replaced: 1.搅拌：无问题 1. Agitator: no issue 2.上口：整体不满足2D 2. Top nozzles: do not meet 2D overall 3.下口：法兰不满足要求； 3. Bottom nozzle: the flange does not meet the requirement; 4.侧口：无 4. Side nozzles: none 罐体大法兰，密封圈为O型圈，满足要 The large vessel flange has an O-ring seal, which meets the requirement | 使用英德150L罐替换。原先80L罐货期长无改造价值，返厂2个月。 Replaced by a Yingde 150 L vessel. The original 80 L vessel has a long lead time and is not worth modifying (2 months at the factory). |  |  | 5d（验证4d+清洗1d） / 5 d (qualification 4 d + cleaning 1 d)
92 | [8 empty] | 管路 / Piping | 1.氮气：无问题 1. Nitrogen: no issue 2.尾气：无问题 2. Off-gas: no issue 3.溶剂：非BPE管道，需更换为BPE管道 3. Solvent: non-BPE piping, has to be changed to BPE piping 4.物料：非BPE管道，需更换为BPE管道 4. Material: non-BPE piping, has to be changed to BPE piping | BPE管路改造时同步调整。 Adjusted together with the BPE piping retrofit. 变径形式需要确认方案 The reducer design has to be confirmed | 28天 / 28 days | 21天 / 21 days
93 | [8 empty] | 仪表 / Instruments | 1.压力： 1. Pressure: 配置按照无异常 the configuration is acceptable 2.温度： 2. Temperature: 配置按照无异常 the configuration is acceptable 3.pH计 3. pH: ： 配置按照无异常 the configuration is acceptable 4.差压/雷达/音叉： 4. Differential pressure / radar / tuning fork: 配置按照无异常 the configuration is acceptable | 新罐仪表已采购，未确认供应商 / The instruments for the new tank are purchased; the supplier is not yet confirmed
94 | [8 empty] | 泵 / Pumps | 计量泵不满足排尽要求，计划更换为四元隔膜泵； The metering pump does not meet the drainability requirement and is planned to be replaced by a four-head diaphragm pump; | BPE管路改造时同步调整。 Adjusted together with the BPE piping retrofit. 变径形式需要确认方案，部分管口管件太小买不到，与厂家沟通 The reducer design has to be confirmed; some nozzles and fittings are too small to buy, and this is being discussed with the vendor | 28天 / 28 days | 21天 / 21 days
95 | [8 empty] | 阀门 / Valves | 全部为隔膜阀，满足需求 / All are diaphragm valves and meet the requirement | N/A
96 |  | 1211-Fd01 | 三合一 / Filter-dryer | 1、设备尺寸DN1200； 1. Equipment size DN1200; 2、罐内设计温度-25~200℃，夹套设计温度-25~220℃； 2. Vessel design temperature −25 to 200 °C, jacket design temperature −25 to 220 °C; 3、罐内设计压力-0.1~0.1MPa；夹套工作压力0.6Mpa； 3. Vessel design pressure −0.1 to 0.1 MPa; jacket operating pressure 0.6 MPa; | 与物料接触：304不锈钢衬C22或C276； Product contact: 304 stainless steel lined with C22 or C276; 夹套：304不锈钢； Jacket: 304 stainless steel; 保温：珍珠岩粉； Insulation: perlite powder; 保温外壳：304不锈钢； Insulation cladding: 304 stainless steel; | 各类有机溶剂、酸、碱等 / Various organic solvents, acids, bases, etc. | 台 / unit | 1 | 设备本体 / Equipment body | 1.搅拌：波纹管同搅拌有缝隙，已经改造完毕。 1. Agitator: there was a gap between the bellows and the agitator; this has already been modified. 2.上口：不满足2D，有3个法兰口 2. Top nozzles: do not meet 2D, there are 3 flanged nozzles 3.下口：母液出口及平衡管口均是法兰结构 3. Bottom nozzles: the mother liquor outlet and the equalising line nozzle are both flanged 4.侧口：无 4. Side nozzles: none | 方案确认完毕，图纸已经反馈厂家。返厂改造需25天； The concept is confirmed and the drawings have been returned to the vendor. The return-to-factory modification takes 25 days; |  |  | 2d（验证1d，清洗1d） / 2 d (qualification 1 d, cleaning 1 d)
97 | [8 empty] | 管路 / Piping | 1.氮气：湿氮气的管路不满足2D要求，不能满足可清洗的方式；需要重新设计管路； 1. Nitrogen: the wet nitrogen piping does not meet the 2D requirement and is not cleanable; the piping has to be redesigned; 2.尾气：无问题 2. Off-gas: no issue 3.溶剂：1个气动快开球阀需更换气动隔膜阀； 3. Solvent: one pneumatic quick-connect ball valve has to be replaced by a pneumatic diaphragm valve; 4.物料：无问题。 4. Material: no issue. | BPE管路改造时同步调整。 Adjusted together with the BPE piping retrofit. 变径形式需要确认方案，部分管口管件太小买不到，与厂家沟通 The reducer design has to be confirmed; some nozzles and fittings are too small to buy, and this is being discussed with the vendor | 28天 / 28 days | 21天 / 21 days
98 | [8 empty] | 仪表 / Instruments | 1.压力： 1. Pressure: 无问题 no issue 2.温度： 2. Temperature: 无问题 no issue 3.pH计 3. pH: ：无 none 4.差压/雷达/音叉：无 4. Differential pressure / radar / tuning fork: none | N/A
99 | [8 empty] | 泵 / Pumps | 无 / None | N/A
100 | [8 empty] | 阀门 / Valves | 2个气动快开球阀（溶剂管路、平衡阀）需更换气动隔膜阀 Two pneumatic quick-connect ball valves (solvent line, equalising valve) have to be replaced by pneumatic diaphragm valves | 阀门已采购，未确认供应商，货期8周 The valves are purchased, the supplier is not yet confirmed, lead time 8 weeks |  | 2天 / 2 days
101 |  | 湿氮气 / Wet nitrogen | 湿氮气 / Wet nitrogen | 100L两台 / 2 × 100 L |  |  |  |  | 设备本体 / Equipment body | 1、设备为法兰结构，调节阀，混合器为法兰连接。不满足BPE要求。 1. The equipment is of flanged design; the control valve and the mixer are flange-connected. This does not meet the BPE requirements. 2、整体清洁死角多，不易清洁。--整体更换，新采购设备本周到货。 2. There are many cleaning dead legs overall and the unit is hard to clean – complete replacement; the newly purchased unit arrives this week. | 设备已经到货一台，本周第二台到货安装，调试 One unit has arrived; the second unit arrives this week for installation and commissioning
102 | [8 empty] | 管路 / Piping | 管路不满足BPE标准，为国标316L. The piping does not meet the BPE standard; it is GB-standard 316L.
103 | [8 empty] | 仪表 / Instruments | 仪表不满足BPE标准， / The instruments do not meet the BPE standard,
104 | [8 empty] | 泵 / Pumps | 不涉及 / Not applicable
105 | [8 empty] | 阀门 / Valves | 阀门为球阀，不满足BPE / The valves are ball valves and do not meet BPE
106 | [8 empty] | 评估 / Assessment | 1、湿氮气2天更换水的有效期研究 1. Study of the hold time for changing the water of the wet nitrogen system every 2 days 2、湿氮气水罐储存有效期研究 2. Study of the storage hold time of the wet nitrogen water vessel | 旧设备失败，计划使用新设备进行。 The trial on the old unit failed; the plan is to use the new unit. 预计完成时间：10月中旬 Expected completion: mid-October
107 | [9 empty] | 湿氮气更换水的转移，加水方式及加水的保护评估，目前一个方案是注水专用桶在局部保护下进行，2、使用无菌袋形式转移。 Assessment of the transfer for the wet nitrogen water change, of the filling method and of the protection during filling; one option is to use a dedicated filling vessel under local protection, the second is to transfer using sterile bags. | 局部排风9月底到货， The local exhaust arrives end of September, 无菌袋9月底到货 the sterile bags arrive end of September
108 |  | 单轴旋分筛 / Single-shaft rotary sifter | 旋分筛 / Rotary sifter | 处理量200kg/h. Throughput 200 kg/h. | SS316L | 固体 / Solids | 台 / unit | 1 | 设备本体 / Equipment body | 客户还未评估确认是否满足使用，目前看不符合BPE要求；配电箱较大且死角较多，整体不满足洁净设计； The customer has not yet assessed and confirmed whether it is fit for use; at present it does not meet the BPE requirements; the electrical panel is large and has many dead legs, so the overall hygienic design is not acceptable; | 待专题同客户讨论 / To be discussed with the customer in a dedicated session
109 | [8 empty] | 管路 / Piping | 1.物料：进料方式客户认同直接在三合一出料口安装，目前不满足该要求，需要降低高度；具体细节待进一步同客户沟通确认。 1. Material: the customer agrees that the charging should be directly at the outlet of the filter-dryer; this is currently not the case and the height has to be lowered; the details still have to be discussed and confirmed with the customer. | 待专题同客户讨论 / To be discussed with the customer in a dedicated session
110 | [8 empty] | 仪表 / Instruments | 1.温度：没有温度探头，但有过程中粉料挤压超温风险。 1. Temperature: there is no temperature probe, although there is a risk of overheating when the powder is compressed during the process. 2.氧气含量：配有在线的检测，接口长，不满足2D要求。 2. Oxygen content: in-line measurement is fitted, but the connection is long and does not meet the 2D requirement. | 待专题同客户讨论 / To be discussed with the customer in a dedicated session
111 | [8 empty] | 泵 / Pumps | 未配置 / Not fitted | N/A
112 | [8 empty] | 阀门 / Valves | 配置分体式蝶阀 / Split-body butterfly valve fitted | N/A
113 |  |  | 区域内的氮气管路阀门 / Nitrogen line valves inside the area | 单个快开截止阀 / Single quick-connect shut-off valve |  |  |  |  | 管路 / Piping | 需要在氮气管路上增加双阀控 / A double valve arrangement has to be added on the nitrogen line | 阀门购买中 / Valves being purchased

## 前期剩余工作 Open Work (hidden)
9788改造施工项及施工计划 / 9788 retrofit work packages and construction plan
|  | 工序 / Activity | 事项 / Item | 设备名称 / Equipment name | 设备编号 / Equipment number | 预计工期 / Estimated duration | 当前进展 / Current status | 影响因素 / Influencing factors | 供应商 / Supplier | 备注 / Remarks
1 | 第一次改造内容 / Scope of the first retrofit | 制备 / Preparation | 制备系统配管（2相配液改3相配液）计量泵进出口改造 Piping of the preparation system (change from 2-phase to 3-phase solution preparation), modification of the metering pump inlets and outlets | 制备配液系统 / Preparation / solution system | HPPC03 | 已完成 / Completed | 缺少的一台计量泵配件已经自己改造完成安装完毕 The missing metering pump part was modified in-house and has been installed | 设备及管路整体安装中，三台5号已经完成，针对发错货的一台计量泵，紧急评估更换316L材质，目前也安装完毕，但调节阀、阻尼器等配件在15号才能到货安装完毕 Equipment and piping are being installed; three units were completed on the 5th; for the metering pump that was delivered incorrectly, an urgent assessment was made to switch to 316L and it is now installed, but the control valve, pulsation dampener and other parts will only arrive and be installed on the 15th | 通博 / Tongbo
2 |  |  | 隔膜阀更换 / Diaphragm valve replacement |  |  | 已完成 / Completed | 已经整体完成到货安装。 / Fully delivered and installed.
3 |  |  | 储罐改造（管口更换、抛光） / Storage tank modification (nozzle replacement, polishing) | 500L喷涂搅拌罐 / 500 L coated agitated vessel | HPPC03-AT01 | 已完成 / Completed | 流量计、仪表安装，配线完成 / Flow meter and instrument installation and wiring completed |  | 浙江诚信 / Zhejiang Chengxin
4 |  |  |  | 500L喷涂搅拌罐 / 500 L coated agitated vessel | HPPC03-AT02 | 已完成 / Completed | 流量计、仪表安装，配线完成 / Flow meter and instrument installation and wiring completed
5 |  |  |  | 316L搅拌罐 / 316L agitated vessel | HPPC03-AT03 | 已完成 / Completed | 罐顶抛光完成，管线配管完成，仪表安装完成 Tank top polishing completed, piping completed, instrument installation completed
6 |  |  |  | 316L搅拌罐 / 316L agitated vessel | HPPC03-AT04 | 已完成 / Completed
7 |  |  |  | 316L搅拌罐 / 316L agitated vessel | HPPC03-AT05 | 已完成 / Completed
8 |  |  |  | 316L搅拌罐 / 316L agitated vessel | HPPC03-AT06 | 已完成 / Completed | 罐顶抛光完成，仪表安装完成，系统至储罐管线配管整体完成 Tank top polishing completed, instrument installation completed, the piping from the system to the storage tank fully completed
9 |  |  |  | 纯水罐 / Purified water tank | HPPC03-T01 | 已完成 / Completed | 罐顶抛光完成，管线配管完成，仪表安装完成，抛光度已经出报告，BPE相关材料厂家收集中； Tank top polishing completed, piping completed, instrument installation completed, the roughness report has been issued, the vendor is collecting the BPE documentation;
10 |  |  |  | 乙腈罐 / Acetonitrile tank | HPPC03-T02 | 已完成 / Completed
11 |  |  |  | 流动相A / Mobile phase A | HPPC03-T03 | 已完成 / Completed
12 |  |  |  | 流动相B / Mobile phase B | HPPC03-T04 | 已完成 / Completed
13 |  |  |  | 组分罐 / Fraction tank | HPPC03-T05 | 已完成 / Completed
14 |  |  |  | 顶样罐 / Top-sample tank | HPPC03-T06 | 已完成 / Completed
15 |  |  |  | 废液罐 / Waste liquid tank | HPPC03-WTK01 | 已完成 / Completed | 改造完成 / Modification completed
16 |  |  |  | 废液罐 / Waste liquid tank | HPPC03-WTK02 | 已完成 / Completed | 已完成 / Completed
18 |  | 超滤 / Ultrafiltration | 储罐及设备安装 / Installation of storage tanks and equipment | 1000L储罐 / 1000 L storage tank | TFF02 | 已完成 / Completed | 已完成 / Completed | 地面已重新制作 / The floor has been redone | 隆玛 / Longma
19 |  |  | 储罐管口改造 / Storage tank nozzle modification | 316L储罐 / 316L storage tank | TFF02-T01 | 已完成 / Completed | 罐顶抛光完成，管线配管完成，仪表安装完成 Tank top polishing completed, piping completed, instrument installation completed | 地面已重新制作 / The floor has been redone | 诚信 / Chengxin
20 |  | 沉淀 / Precipitation | 管口改造 / Nozzle modification | 2000L哈氏合金釜 / 2000 L Hastelloy reactor | 1211-R01 | 已完成 / Completed |  | 地面制作中 / Floor work in progress | 诚信 / Chengxin
21 |  |  |  | 600L搅拌罐 / 600 L agitated vessel | 1211-AT01 | 已完成 / Completed | 整体配管已完成，剩余新增的单独高低温一体机夹套管路制作中，预计09/03/2026完成。 All piping is completed; the jacket piping for the additional stand-alone hot / cold TCU is still being fabricated and is expected to be finished on 09/03/2026. | 地面制作中 / Floor work in progress | 浙江诚信 / Zhejiang Chengxin
22 |  |  |  | DN1200哈氏合金三合一 / DN1200 Hastelloy filter-dryer | 1211-FD01 | 已完成 / Completed | 罐顶抛光完成，管线配管完成，仪表安装完成 Tank top polishing completed, piping completed, instrument installation completed | 地面制作中 / Floor work in progress | 隆玛 / Longma
23 |  | 洁净区 / Clean area | 隐蔽工程改造 / Concealed works modification | 防爆灯 / Explosion-proof lighting |  | 已完成 / Completed | 更换完成 / Replacement completed
24 |  |  |  | 防爆断路器 / Explosion-proof circuit breaker |  | 已完成 / Completed | 安装完成 / Installation completed
25 |  |  |  | 温湿度计 / Temperature / humidity sensor |  | 已完成 / Completed | 安装完成 / Installation completed
26 |  |  |  | 互锁 / Interlocks |  | 已完成 / Completed | 更换完成 / Replacement completed
27 |  |  |  | 不锈钢仪表 / Stainless-steel instruments |  | 已完成 / Completed | 更换完成 / Replacement completed
28 |  |  |  | AP、电话 / Wi-Fi access point, telephone |  | 已完成 / Completed | 更换完成 / Replacement completed
29 |  |  |  | 消防设施 / Fire-fighting installations |  | 已完成 / Completed | 更换完成 / Replacement completed
30 | 第二次新增需求 / Additional requirements, second round | 制备 / Preparation | 新增TCU1台 / Add one TCU |  | HPP03-TCU03 | 已完成 / Completed | TCU01/02/03现场调试中 TCU01 / 02 / 03 are being commissioned on site |  | 通博 / Tongbo
31 |  |  | 原先的2个500L Halar盐罐调整为300L、500L HC盐罐—BLA对应设备材质的要求； The two original 500 L Halar-lined salt tanks are changed to a 300 L and a 500 L Hastelloy salt tank – BLA requirement on the equipment material; |  |  | 已完成 / Completed | 已完成 / Completed |  | 通博 / Tongbo
32 |  |  | 两个盐罐的配液泵对换安装； / Swap the installation of the solution transfer pumps of the two salt tanks; |  |  | 已完成 / Completed | 已完成 / Completed |  | 通博 / Tongbo
33 |  |  | 增加3000L组分罐至8000L组分罐转移质量流量计。 Add a mass flow meter for the transfer from the 3000 L fraction tank to the 8000 L fraction tank. |  |  | 已完成 / Completed | 图纸取消 / Cancelled in the drawings |  | 通博 / Tongbo
34 |  |  | 增加8000L组分罐去上样罐的过滤器， Add a filter in the line from the 8000 L fraction tank to the loading vessel, |  |  | 已完成 / Completed | 图纸取消 / Cancelled in the drawings |  | 通博 / Tongbo
35 |  |  | 组分接收口4取消进组分桶，接收9口由原先进废液罐改成进组分桶，接收10口进高杂/低杂，增加三通进行切换 Fraction receiving port 4 no longer feeds the fraction drum; receiving port 9 is changed from the waste liquid tank to the fraction drum; receiving port 10 feeds the high-impurity / low-impurity streams, with an additional tee for switching |  |  | 已完成 / Completed | 整改完成 / Rectification completed |  | 通博 / Tongbo
36 |  | 超滤 / Ultrafiltration | 新增2根溶剂管道 / Add 2 solvent lines |  |  | 已完成 / Completed | 整改完成 / Rectification completed |  | 隆玛 / Longma
37 |  | 沉淀 / Precipitation | 新增80L、600L搅拌罐 / Add the 80 L and 600 L agitated vessels |  |  | 已完成 / Completed | 整体配管已完成 / All piping completed | 泵发货延误6天，安全配件延误10天； The pump shipment was 6 days late and the safety accessories 10 days late; | 隆玛 / Longma
38 |  |  | 新增湿氮气 / Add the wet nitrogen system |  |  | 已完成 / Completed | 点位制作完成 / Tie-in points completed |  | 隆玛 / Longma
39 |  | 物料转移 / Material transfer | 增加一台3000L HC釜，同步配置转移至配液间管路，增加在线pH计，纯化水气动开关阀和调节阀改成手阀； Add one 3000 L Hastelloy reactor, together with the transfer piping to the solution preparation room, add an in-line pH meter, and change the pneumatic on/off valve and control valve of the purified water to manual valves; |  |  | 2026-09-17 | 纯化水管线施工已完成，流量计已安装待接线，蒸馏管材到货暂未施工 The purified-water line is installed, the flow meter is installed and waiting for wiring; the pipe material for the distilled-water line has arrived but the work has not started yet | 目前沟通厂家，反应釜下口改造BPE快开，尺寸不一致，先进行法兰连接，涉及压力容器事项，厂家到厂改造 The vendor is being consulted; converting the reactor bottom outlet to a BPE quick-connect does not match the size, so a flanged connection is used first; as a pressure-vessel matter, the vendor will carry out the modification on site | 通博 / Tongbo
40 |  |  | 制备到超滤物料转移管路 / Material transfer line from the preparative system to ultrafiltration |  |  | 已完成 / Completed | 坡度已调整完成 / The slope has been adjusted |  | 隆玛 / Longma
41 |  |  | 新增超滤到釜物料转移管路 / Add the material transfer line from ultrafiltration to the reactor |  |  | 已完成 / Completed | 坡度已调整完成 / The slope has been adjusted |  | 隆玛 / Longma
42 |  |  | 制备液到制备机以及收集储罐系统的 From the prepared solution to the preparative unit and the collection tank system |  |  | 已完成 / Completed | 管道酸洗钝化将部分管件拆除，等酸洗钝化完成后重新调坡度 Some fittings were removed for pickling and passivation of the piping; the slope will be readjusted once pickling and passivation are finished | HPPC03-AT03、HPPC03-AT04、HPPC03-AT05 HPPC03-AT03, HPPC03-AT04, HPPC03-AT05
43 |  |  | 超滤系统、沉淀系统设备转移管路 Equipment transfer piping of the ultrafiltration and precipitation systems |  |  | 已完成 / Completed | 超滤系统调整完毕，沉淀系统持续进行 The ultrafiltration system is finished; the precipitation system is ongoing | TFF02、TFF02-T01、1211-R01 TFF02, TFF02-T01, 1211-R01
44 | 第三次新增需求 / Additional requirements, third round | 制备 / Preparation | 1000L储罐和1000L搅拌罐功能调换，安装位置调换 Swap the functions and the installation positions of the 1000 L storage tank and the 1000 L agitated vessel |  |  | 已完成 / Completed | 已改造完成 / Modification completed |  | 通博 / Tongbo
45 |  |  | 1000L组分搅拌罐/3000L上样罐增加乙腈管路点位 Add acetonitrile line tie-ins for the 1000 L fraction agitated vessel / 3000 L loading vessel |  |  | 已完成 / Completed | 已改造完成 / Modification completed |  | 通博 / Tongbo
46 |  |  | 1000L组分搅拌罐/3000L上样罐增加纯化水管路点位 Add purified-water line tie-ins for the 1000 L fraction agitated vessel / 3000 L loading vessel |  |  | 已完成 / Completed | 已改造完成 / Modification completed |  | 通博 / Tongbo
47 |  |  | 增加组分接收桶合格组分转移至1000L组分搅拌罐管路 Add the line transferring in-spec fractions from the fraction receiving drum to the 1000 L fraction agitated vessel |  |  | 已完成 / Completed | 已改造完成 / Modification completed |  | 通博 / Tongbo
48 |  |  | 3000L组分罐往8000L组分罐转移管路增加3000L自循环清洗管路 Add a 3000 L recirculation cleaning line to the transfer line from the 3000 L fraction tank to the 8000 L fraction tank |  |  | 已完成 / Completed | 已改造完成 / Modification completed |  | 通博 / Tongbo
49 |  |  | 8000L组分罐至TFF的1000L中转罐增加质量流量计 Add a mass flow meter in the line from the 8000 L fraction tank to the 1000 L intermediate tank of the TFF skid |  |  | 已完成 / Completed | 预计9月10日 / Expected on 10 September | 已到货，已检验完毕，待车间验证可进人后安装完毕 Delivered and inspected; installation will be completed once the workshop is released for personnel access | 通博 / Tongbo
1、制备区5号完成施工；（3号完成管路安装，4号晚到泵配件，预计5号完成） 1. Preparation area: construction finished on the 5th (piping installation finished on the 3rd; the pump parts arrived late on the 4th, completion expected on the 5th) 2、超滤区10号完成；流量计预计10号到货；（1号完成管路安装） 2. Ultrafiltration area: finished on the 10th; the flow meter is expected on the 10th (piping installation finished on the 1st) 3、沉淀区5号完成施工；（3号完成管路安装，4号晚到泵配件，预计5号完成） 3. Precipitation area: construction finished on the 5th (piping installation finished on the 3rd; the pump parts arrived late on the 4th, completion expected on the 5th) 4、新增四层釜到制备物料转移管路预计15号前完成（需求时间），流量计预计10号到货，CNC区域不影响C区域验证； 4. The new material transfer line from the level-4 reactor to the preparative system is expected to be finished before the 15th (required date); the flow meter is expected on the 10th; the CNC area does not affect the qualification of area C 5、1号做超滤地面，2号沉淀区地面，3号3、4楼改造区地面 5. Ultrafiltration floor on the 1st, precipitation area floor on the 2nd, floors of the retrofit areas on levels 3 and 4 on the 3rd
|  | 工序 / Activity | 事项 / Item | 设备名称 / Equipment name | 设备编号 / Equipment number | 预计工期 / Estimated duration | 当前进展 / Current status | 影响因素 / Influencing factors | 供应商 / Supplier | 备注 / Remarks
50 | 第四次新增需求 / Additional requirements, fourth round | 制备 / Preparation | 后续制备配液系统、超滤、沉淀设备BPE方式变更 Subsequent change of the preparation / solution system, ultrafiltration and precipitation equipment to BPE design | 储罐、反应釜、三合一、配套的管路、泵体、计量表、阀门 Storage tanks, reactors, filter-dryer, associated piping, pumps, meters and valves | N/A | 设备采购货期100天，安装3周时间，整体安装需要4个月，验证时间预计2-3周。 Equipment procurement lead time 100 days, installation 3 weeks, total installation 4 months, qualification expected to take 2–3 weeks. | 制备更换BPE管件已全部采购出去，报价中，货期5周； All BPE fittings for the preparation area have been issued for purchase and are being quoted, lead time 5 weeks; 需更换的泵，316L四元隔膜泵已采购，货期约；316L卫生级离心泵已采购预计10月下旬到货； of the pumps to be replaced, the 316L four-head diaphragm pumps are purchased, lead time approx.; the 316L sanitary centrifugal pumps are purchased and expected in the second half of October; 自控阀门议价中，还未确认厂家； the automated valves are under price negotiation and the vendor is not yet confirmed; 流量计已下单，10月18号到货； the flow meters are ordered, arriving on 18 October; 自控仪表已下单，10月15号到货； the automation instruments are ordered, arriving on 15 October; | 釜、三合一、储罐客户基本认可，R05釜、及AT01、AT02罐存在法兰接口需更换为快开形式，因涉及压力容器，厂家到厂进行改造，改造方案已基本确认，预计10月15号到厂改造 The customer broadly accepts the reactors, filter-dryer and storage tanks; reactor R05 and tanks AT01 and AT02 have flanged connections that have to be changed to quick-connect; as pressure vessels are involved, the vendor will carry out the modification on site; the modification concept is largely confirmed and the vendor is expected on site on 15 October | 李延龙 Li Yanlong 张暴 Zhang Bao 王志恒 Wang Zhiheng
51 |  |  | 制备系统 / Preparation system | 制备机 / Preparative chromatography unit | 纯化分离HPPC03 / Purification / separation HPPC03 | 阀门已经订货，预计10月10号到货，施工10-15天 The valves are ordered and expected on 10 October; construction 10–15 days | 同厂家确认不满足该要求，同步采购并要求厂家过来改造； Confirmed with the vendor that the requirement is not met; the parts are being purchased and the vendor is asked to come and modify the unit; | 说明制备系统本身使用球阀和非T-C接口的合理性，球阀需要使用无滞留腔的球阀（腔体填充式）——这个之前没有提到过，安排进行评估，目前不满足 Explain why ball valves and non-TC connections are acceptable on the preparative system itself; the ball valves have to be of the cavity-filled type without hold-up – this was never mentioned before, an assessment has been arranged, and the current design does not comply | 范兴涛 Fan Xingtao 高磊 Gao Lei
52 |  |  | 制备配液系统 / Preparation / solution system | HPPC03 | 制备系统的在线三相配制流动相 / In-line three-phase mobile phase preparation of the preparative system | BPE管件28天；BPE阀门42天，设备材料到货后施工15天 BPE fittings 28 days; BPE valves 42 days; 15 days of construction after the equipment and materials arrive | 制备更换BPE管件已全部采购出去，316L材料第一批预计10月10号到货，第二批货期未提供；哈氏合金材料第一批预计11月13号到货，第二批货期未提供； All BPE fittings for the preparation area have been issued for purchase; the first batch of 316L material is expected on 10 October, no lead time given for the second batch; the first batch of Hastelloy material is expected on 13 November, no lead time given for the second batch; 涉及2D排放的采购了20个T型阀门，预计10月25号到货； 20 T-valves were purchased for the 2D drain points, expected on 25 October; | 管线中存在法兰结构；法兰调节阀； There are flanged connections in the lines, including flanged control valves; 管线中涉及到的计量泵及对应阻尼器、调节阀，安全阀不满足洁净卫生要求；管线不满足BPE标准；排尽点及三通不满足2D标准 the metering pumps in the lines and the associated pulsation dampeners, control valves and safety valves do not meet the hygienic requirements; the lines do not meet the BPE standard; the drain points and tees do not meet the 2D standard | 宋金柱/通博 / Song Jinzhu / Tongbo
53 |  |  | 3000L哈氏合金釜 / 3000 L Hastelloy reactor | 1213-R05 | 配制1M浓盐溶液（Tris和乙酸铵） Preparation of 1 M concentrated salt solution (Tris and ammonium acetate) | 方案一：利旧多肽3预计10月底到货 Option 1: reuse the unit from Peptide Building 3, expected end of October 方案二：返厂改造60天（厂家未反馈准确时间，参考多肽3），多次与供货商沟通无法现场改造； Option 2: return-to-factory modification, 60 days (the vendor has not confirmed an exact time; based on Peptide Building 3). Repeated discussions with the vendor confirmed that on-site modification is not possible. 方案三：新采购100天； BPE管件28天；BPE阀门42天，设备材料到货后施工15天 Option 3: buy new, 100 days; BPE fittings 28 days; BPE valves 42 days; 15 days of construction after the equipment and materials arrive | 釜下口法兰改为快开，HC材质，与厂家确认完方案，预计10月15号到货现场改造，改造周期10天； The flanged reactor bottom outlet is converted to quick-connect in Hastelloy; the concept is agreed with the vendor; the parts are expected on 15 October for the on-site modification, which takes 10 days; 下口管路按316L.BPE标准安装，已安装完成 the bottom outlet piping is installed to 316L BPE standard and is already finished | 管线中存在法兰结构；法兰调节阀； There are flanged connections in the lines, including flanged control valves; 管线中涉及到的计量泵及对应阻尼器、调节阀，安全阀不满足洁净卫生要求；管线不满足BPE标准；排尽点及三通不满足2D标准 the metering pumps in the lines and the associated pulsation dampeners, control valves and safety valves do not meet the hygienic requirements; the lines do not meet the BPE standard; the drain points and tees do not meet the 2D standard | 宋金柱/通博/诚信 / Song Jinzhu / Tongbo / Chengxin
54 |  |  | 300L哈氏合金搅拌罐 / 300 L Hastelloy agitated vessel | HPPC03-AT01 | 储存1M浓盐溶液（Tris和乙酸铵） Storage of 1 M concentrated salt solution (Tris and ammonium acetate) | 方案一：使用英德316L储罐改造40天（前提是可以使用316L材质，生产评估中）； Option 1: modify a Yingde 316L storage tank, 40 days (provided that 316L is acceptable; under assessment by Production) 方案二：返厂改造60天（厂家未反馈准确时间，参考多肽3）； Option 2: return-to-factory modification, 60 days (the vendor has not confirmed an exact time; based on Peptide Building 3) 方案三：新采购100天：BPE管件28天；BPE阀门42天，设备材料到货后施工15天 Option 3: buy new, 100 days: BPE fittings 28 days; BPE valves 42 days; 15 days of construction after the equipment and materials arrive | 釜上下口法兰改为快开，HC材质，与厂家确认完方案，预计10月15号到货现场改造，改造周期10天； The flanged top and bottom nozzles of the vessel are converted to quick-connect in Hastelloy; the concept is agreed with the vendor; the parts are expected on 15 October for the on-site modification, which takes 10 days; | 管线中存在法兰结构；法兰调节阀； There are flanged connections in the lines, including flanged control valves; 管线中涉及到的计量泵及对应阻尼器、调节阀，安全阀不满足洁净卫生要求；管线不满足BPE标准；排尽点及三通不满足2D标准 the metering pumps in the lines and the associated pulsation dampeners, control valves and safety valves do not meet the hygienic requirements; the lines do not meet the BPE standard; the drain points and tees do not meet the 2D standard | 宋金柱/通博/诚信 / Song Jinzhu / Tongbo / Chengxin
55 |  |  | 500L哈氏合金搅拌罐 / 500 L Hastelloy agitated vessel | HPPC03-AT02 | 储存250mM浓盐溶液（Tris和乙酸铵） Storage of 250 mM concentrated salt solution (Tris and ammonium acetate) |  | 釜上下口法兰改为快开，HC材质，与厂家确认完方案，预计10月15号到货现场改造，改造周期10天； The flanged top and bottom nozzles of the vessel are converted to quick-connect in Hastelloy; the concept is agreed with the vendor; the parts are expected on 15 October for the on-site modification, which takes 10 days; | 管线中存在法兰结构；法兰调节阀； There are flanged connections in the lines, including flanged control valves; 管线中涉及到的计量泵及对应阻尼器、调节阀，安全阀不满足洁净卫生要求；管线不满足BPE标准；排尽点及三通不满足2D标准 the metering pumps in the lines and the associated pulsation dampeners, control valves and safety valves do not meet the hygienic requirements; the lines do not meet the BPE standard; the drain points and tees do not meet the 2D standard | 宋金柱/通博/诚信 / Song Jinzhu / Tongbo / Chengxin
56 |  |  | 表面粗糙度 / Surface roughness | 1000L储罐 / 1000 L storage tank |  | 已完成 / Completed | 尽快完成抛光 / Complete the polishing as soon as possible | 搅拌上封头有焊接痕迹，局部抛光不彻底。 There are weld marks on the upper head at the agitator and the local polishing is incomplete. | 宋金柱 / Song Jinzhu
57 |  |  | 阀门选型 / Valve selection | 超滤系统 / Ultrafiltration system |  | 超滤间与制备间阀门调整完成，结晶间16日进行调整 The valves in the ultrafiltration and preparation rooms are adjusted; the crystallisation room will be adjusted on the 16th | 各房间阀门数量已统计完，阀门已采购，询价中 The valve quantities per room have been counted; the valves are purchased and quotations are being obtained | 排废阀门使用的快开阀门，表面有清洁死角 The waste drain valves are quick-connect valves with cleaning dead legs on the surface | QA/宋金柱 / QA / Song Jinzhu
58 |  |  | 超滤过滤器更换 / Replacement of the ultrafiltration filter | 超滤系统 / Ultrafiltration system |  | 已完成 / Completed | 后面有冗余过滤器，该处过滤器直接更改短接。 There is a redundant filter downstream, so this filter is simply replaced by a spool piece. | 超滤进料过滤器更换会有物料暴露 Replacing the ultrafiltration feed filter would expose the product | 宋金柱 / Song Jinzhu
59 |  |  | 下磁力搅拌电机 / Bottom magnetic agitator motor | 超滤循环罐 / Ultrafiltration recirculation vessel |  | 已完成 / Completed | 统一排查进行除锈完成 / All items have been checked and the rust removal is completed | 部分螺丝有锈迹 / Some bolts show rust | 郭泽鹏 / Guo Zepeng
60 |  |  | 阀门安装角度 / Valve installation angle | 超滤系统 / Ultrafiltration system |  | 已完成 / Completed | 超滤间与制备间阀门调整完成，结晶间16日进行调整 The valves in the ultrafiltration and preparation rooms are adjusted; the crystallisation room will be adjusted on the 16th | 现场隔膜阀正在调节 / The diaphragm valves are being adjusted on site | 宋金柱/隆玛 / Song Jinzhu / Longma
61 |  | 沉淀 / Precipitation | 600L搅拌罐 / 600 L agitated vessel | 1211-AT01 | 体系成盐 / Salt formation of the system | 此次客户到厂后，提出排净要求，艾力普计量泵可以使用 During the customer's latest visit a drainability requirement was raised; the Ailipu metering pumps can be used | 新BPE罐子以上预算采购，询价中 The new BPE vessels are submitted for budget and purchase; quotations are being obtained | 管线中存在计量泵及对应阻尼器、调节阀，安全阀不满足洁净卫生要求；排尽点及三通不满足2D标准 The lines contain metering pumps whose pulsation dampeners, control valves and safety valves do not meet the hygienic requirements; the drain points and tees do not meet the 2D standard | 宋金柱 王志恒 Song Jinzhu Wang Zhiheng
62 |  |  | 氮气加湿器 / Nitrogen humidifier | 终产品三合一烘料 / Final product drying in the filter-dryer | 终产品三合一烘料加湿氮气 / Wet nitrogen for the final product drying in the filter-dryer | 方案已经确认，预算上报审批中，新的氮气加湿已经到后，后续安排验证 The concept is confirmed and the budget is under approval; the new nitrogen humidifier has arrived and qualification will be scheduled | 磁启安装完毕；层流保护配置，16号到货； The magnetic starter is installed; the laminar flow protection is configured and arrives on the 16th; | 湿氮气设备安装后，新增湿氮装置打水保护、层流配置 After the wet nitrogen unit is installed, the water filling protection and the laminar flow configuration of the new humidifier will be added | 李延龙 Li Yanlong 周洪如 Zhou Hongru 宋金柱 Song Jinzhu
63 |  |  | 管路安装标准 / Piping installation standard | 三合一 / Filter-dryer | 1211-FD01 | 已完成 / Completed | 三合一平台上DN25转移管路安装存在歪的情况，可能是安装过程尺寸导致 The DN25 transfer line on the filter-dryer platform is installed slightly out of line, probably because of the dimensions during installation | 调整管路 / Realign the piping | 宋金柱/隆玛 / Song Jinzhu / Longma
64 |  |  | 软管选型 / Hose selection | 三合一搅拌 / Filter-dryer agitator | 1211-FD01 | 已完成 / Completed | 管路为金属编制软管，存在清洁死角 The line is a metal-braided hose, which has cleaning dead legs | 更改为无死角形式 / Change to a design without dead legs | 宋金柱 / Song Jinzhu
65 |  |  | 管支架标准 / Pipe support standard | 2000L哈氏合金 / 2000 L Hastelloy reactor |  | 已完成 / Completed | 管支架仍存在旧的有死角的支架 / Some old pipe supports with dead legs are still in place | 更改为目前整改的形式 / Change to the design used in the current rectification | 宋金柱 / Song Jinzhu
66 |  |  | DN1200哈氏合金三合一 / DN1200 Hastelloy filter-dryer | 1211-FD01 | 过滤&烘料 / Filtration and drying | 已完成 / Completed | 厂家进行焊接打磨完成 / The vendor has completed the welding and grinding | 三合一搅拌轴部存在缝隙，有死角残留风险 There is a gap at the agitator shaft of the filter-dryer, with a risk of hold-up in the dead leg | 范兴涛 Fan Xingtao 高磊 Gao Lei
67 |  | 洁净区隐蔽工程改造 / Concealed works modification in the clean area | 地漏 / Floor drain | 洁净区 / Clean area | 车间环境需求 / Workshop environment requirement | 已完成 / Completed | QA需要评估复核要求 / QA has to assess and review the requirement | 现场新增问题： New points raised on site: 1、C级区地漏暂无优先的选择 1. No preferred solution is available yet for the floor drain in the Grade C area 2、空调的回风管道保温，避免凝水； 2. Insulate the HVAC return air duct to avoid condensation; 3、减速机及电机罩已进行打胶 3. The gearbox and motor covers have been sealed with silicone 4、底角螺栓已制作盖帽，已打胶 4. Caps have been made for the foot bolts and sealed with silicone 5、隔膜阀角度正在根据验证要求调整中 5. The diaphragm valve angles are being adjusted according to the qualification requirements 6、现场制备的保温，使用发泡填充夹套 6. For the insulation prepared on site, the jacket is filled with foam 7、DCS无菌键盘已全部更换完成 7. All DCS aseptic keyboards have been replaced 8、纯化水管线的管支架已全部制作 8. All pipe supports for the purified-water lines have been made 9、穿墙管，穿平台的管，客户觉得有清洁死角，需要考虑更改其他形式。 9. The customer considers that the wall and platform penetrations have cleaning dead legs, so an alternative design has to be considered. | 宋金柱 / Song Jinzhu
68 |  |  | 回风管 / Return air duct |  | 车间环境需求 / Workshop environment requirement | 2-3周后续改造 / Modification in 2–3 weeks | 增加保温，可暂缓，解决重点急迫问题后进行 Add insulation; can be deferred and done once the urgent priorities are solved |  | 宋金柱 / Song Jinzhu
69 |  |  | 减速机罩子 / Gearbox cover |  | 车间环境需求 / Workshop environment requirement | 已完成 / Completed | 匀浆罐已完成整改 / The homogenisation vessel is rectified |  | 宋金柱 / Song Jinzhu
70 |  |  | 气动泵安装 / Pneumatic pump installation |  | 车间环境需求 / Workshop environment requirement | 已完成 / Completed | 气动泵，底角螺栓盖已安装 / Pneumatic pumps: the foot bolt caps are installed |  | 宋金柱 / Song Jinzhu
71 |  |  | 隔膜阀方向 / Diaphragm valve orientation |  | 车间环境需求 / Workshop environment requirement | 已完成 / Completed | 洁净间无法进入 / The clean room cannot be entered |  | 宋金柱 Song Jinzhu 郭泽鹏 Guo Zepeng
72 |  |  | 保温 / Insulation |  | 车间环境需求 / Workshop environment requirement | 已完成 / Completed | 保温拆除已完成 / The insulation removal is completed |  | 郭泽鹏 / Guo Zepeng
73 |  |  | 键盘 / Keyboards |  | 车间环境需求 / Workshop environment requirement | 已完成 / Completed | 14日更换完成 / Replacement completed on the 14th |  | 宋金柱 Song Jinzhu 范兴涛 Fan Xingtao
74 |  |  | 纯水支架 / Purified-water pipe supports |  | 车间环境需求 / Workshop environment requirement | 已完成 / Completed | 已完成安装 / Installation completed |  | 宋金柱 / Song Jinzhu
75 |  |  | 穿墙护套 / Wall penetration sleeve |  | 车间环境需求 / Workshop environment requirement | 正在寻找采购护套预计09/13/2026 Sourcing the sleeves; expected 09/13/2026 | 待客户检查结束后确认改造形式，进行动火更换 The modification design will be confirmed after the customer's inspection and then executed as hot work |  | 宋金柱 Song Jinzhu 范兴涛 Fan Xingtao
76 |  |  | 静电扁铁 / Earthing flat bar |  | 车间环境需求 / Workshop environment requirement | 先按目前形式执行，本次9月15号客户排查没有在提出来 Keep the current design for now; the customer did not raise it again during the inspection on 15 September | 静电扁铁形式比较突兀，客户反馈看下是否有更好的形式。 The earthing flat bar looks rather obtrusive; the customer was asked whether there is a better design. | 客户再去礼来看一下标准 / The customer will check the standard at Eli Lilly again | 李更凯 / Li Gengkai
77 |  |  | 氮气接口 / Nitrogen connection |  | 车间环境需求 / Workshop environment requirement | 阀门采购中，进行增加双阀 / Valves are being purchased; a double valve arrangement will be added | 快开阀门已提报流程 / The request for the quick-connect valves has been submitted | 正在询价确认货期 / Quotations and lead times are being confirmed | 李更凯 宋金柱 Li Gengkai Song Jinzhu
78 |  |  | 喷淋烟感 / Sprinklers and smoke detectors |  | 车间环境需求 / Workshop environment requirement | 已完成 / Completed | 应该有隐藏式的，目前咱们的并不是 There should be a concealed type; the current one is not | 甲类的使用不了 / Not usable in a Class A (explosive) area | 宋金柱 / Song Jinzhu
79 |  |  | 管路安装标准 / Piping installation standard |  | 车间环境需求 / Workshop environment requirement | 减少不必要快开卡接，已完成 / Reduce unnecessary quick-connect clamps; completed | 尽量减少快开接口数量，比如很短一根直管有多处快开卡箍；后续制作的管道尽可能焊接形式 Minimise the number of quick-connect connections, for example a very short straight pipe with several quick-connect clamps; piping made in future shall be welded wherever possible | 后续管线减少快开连接，尽可能自动焊接 Reduce quick-connect connections in future piping and use automatic welding wherever possible | 宋金柱 / Song Jinzhu
81 |  |  | 应急灯、疏散通道标识的罩 / Covers for emergency lights and escape route signs |  | 车间环境需求 / Workshop environment requirement | 已完成 / Completed | 进行拆除整改完成 / Removal and rectification completed | 09/07/2026 | 宋金柱 / Song Jinzhu

## 辅助设备 Auxiliary Equipment (hidden)
辅助设备 / Auxiliary equipment
一、设备采购清单 / I. Equipment purchasing list
序号 / No. | 设备/仪表/阀门 / Equipment / instrument / valve | 技术参数 / Technical parameters | 单位 / Unit | 数量 / Quantity | 备注 / Remarks | 备注 / Remarks
1 | 过滤器 / Filter housing | 单芯，5英寸，BPE / Single cartridge, 5 inch, BPE | 台 / unit | 50
2 | 过滤器 / Filter housing | 单芯，10英寸，BPE / Single cartridge, 10 inch, BPE | 台 / unit | 20
3 | 过滤器 / Filter housing | 三芯，10英寸，BPE / Triple cartridge, 10 inch, BPE | 台 / unit | 20
4 | 局部层流 / Local laminar flow unit | C级标准， / Grade C standard, | 台 / unit | 1
5 | 注射水管 / Water-for-injection hose | 硫化铂金，BPE / Platinum-cured silicone, BPE | 根 / piece | 20
6 | 滤芯 / Filter cartridge | PTFE亲水,10英寸 / PTFE hydrophilic, 10 inch | 根 / piece | 100
7 | 滤芯 / Filter cartridge | PTFE疏水,10英寸 / PTFE hydrophobic, 10 inch | 根 / piece | 60